## Main Menu
Main Menu
Highlands105A Stage 1 D_DBPR Reports.xls - Version 1.01
Reporting Forms for the Stage 1 D/DBPR
TOC Monitoring Report
Worksheet for reporting source water TOC & Alkalinity and treated/filtered water TOC.
This worksheet only applies to conventional water treatment facilities.
Information on TOC regulations (Steps 1 & 2 and alternative compliance).
TTHM and HAA5 Monitoring Reports
Worksheet for reporting TTHM and HAA5 (quarterly monitoring).
For water systems that have up to four distribution sample sites and will
monitor sites on same day and month.
Chlorine Monitoring Report
Worksheet for reporting chlorine residual in distribution system.
Analytical Methods
Analytical Methods for TTHM, HAA5, TOC, Free Chlorine, Chloramines & Bromate.
Note: Each report calculates quarterly averages and running annual average (RAA).
There is no chlorine dioxide monitoring plan in this program.
The reports in this program do not cover all monitoring scenarios for systems in California.
For any questions, please contact the Mendocino District @ 707-576-2145.

## TOC Plan1
Berryessa Highlands
DBP Precursor Removal Compliance Calculations For Water Utility
Enhanced Coagulation - Year 1
Year: | 2015
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No?
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio | [16 empty] | Source Water |  | Treated
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4 | [14 empty] | Month | Day | Alk | TOC | Water TOC |  | TOC | Water TOC | Alk
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters) |  |  | >2.0-4.0 | >4.0-8.0 | >8.0 |  | >2.0-4.0 | >4.0-8.0 | >8.0 | [7 empty] | (mg/L) | (mg/L) | (mg/L) |  | (mg/L) | (mg/L) | (mg/L)
January | [10 empty] | - | 0 | 0.35 | 0.45 | 0.5 | 0 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | January | 22 | 68 | 17 | 5.6 | 2002-01-22 | 17 | 5.6 | 68
February | [11 empty] | 5 | 0.35 | 0.45 | 0.5 | 5 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | February | 21 | 76 | 8.6 | 4.8 | 2002-02-21 | 8.6 | 4.8 | 76
March | [9 empty] | - |  | 10 | 0.35 | 0.45 | 0.5 | 10 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | March | 20 | 112 | 7.1 | 2.8 | 2002-03-20 | 7.1 | 2.8 | 112
April | [10 empty] | - | 15 | 0.35 | 0.45 | 0.5 | 15 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | April | 18 | 117 | 2.9 | 1.9 | 2002-04-18 | 2.9 | 1.9 | 117
May | [11 empty] | 20 | 0.35 | 0.45 | 0.5 | 20 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | May | 17 | 110 | 3 | 1.7 | 2002-05-17 | 3 | 1.7 | 110
June | [9 empty] | - |  | 25 | 0.35 | 0.45 | 0.5 | 25 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | June | 19 | 118 | 3 | 1.7 | 2002-06-19 | 3 | 1.7 | 118
July | [10 empty] | - | 30 | 0.35 | 0.45 | 0.5 | 30 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | July | 17 | 98 | 3 | 1.4 | 2002-07-17 | 3 | 1.4 | 98
August | [11 empty] | 35 | 0.35 | 0.45 | 0.5 | 35 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | August | 21 | 106 | 2.7 | 1.8 | 2002-08-21 | 2.7 | 1.8 | 106
September | [9 empty] | - |  | 40 | 0.35 | 0.45 | 0.5 | 40 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | September | 18 | 120 | 2.9 | 1.9 | 2002-09-18 | 2.9 | 1.9 | 120
October | [10 empty] | - | 45 | 0.35 | 0.45 | 0.5 | 45 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | October | 16 | 94 | 2.1 | 1 | 2002-10-16 | 2.1 | 1 | 94
November | [11 empty] | 50 | 0.35 | 0.45 | 0.5 | 50 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | November | 20 | 86 | 7 | 1 | 2002-11-20 | 7 | 1 | 86
December | [11 empty] | 55 | 0.35 | 0.45 | 0.5 | 55 | 0.35 | 0.45 | 0.5 |  |  |  |  | 0 | December | 31 | 65 | 4 | 3 | 2002-12-31 | 4 | 3 | 65
[12 empty] | 60 | 0.35 | 0.45 | 0.5 | 60 | 0.35 | 0.45 | 0.5 | [5 empty] | January | 29 | 62 | 17 | 9 | 2003-01-29 | 17 | 9 | 62
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter. | [11 empty] | 60.5 | 0.25 | 0.35 | 0.4 | 60.5 | 0.25 | 0.35 | 0.4 | [5 empty] | February | 19 | 88 | 20 | 12 | 2003-02-19 | 20 | 12 | 88
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than | [11 empty] | 65 | 0.25 | 0.35 | 0.4 | 65 | 0.25 | 0.35 | 0.4 | [5 empty] | March
or equal to 1.00, then the system is in compliance with the TOC removal requirements. | [11 empty] | 70 | 0.25 | 0.35 | 0.4 | 70 | 0.25 | 0.35 | 0.4 | [5 empty] | April
[12 empty] | 75 | 0.25 | 0.35 | 0.4 | 75 | 0.25 | 0.35 | 0.4 | [5 empty] | May | 21 | 150 | 5 | 3 | 2003-05-21 | 5 | 3 | 150
Treated Water TOC Sample Location: |  |  |  | Post Filtration | [7 empty] | 80 | 0.25 | 0.35 | 0.4 | 80 | 0.25 | 0.35 | 0.4 | [5 empty] | June | 18 | 126 | 5.8 | 3.1 | 2003-06-18 | 5.8 | 3.1 | 126
[12 empty] | 85 | 0.25 | 0.35 | 0.4 | 85 | 0.25 | 0.35 | 0.4 | [5 empty] | July | 16 | 118 | 4.5 | 3.9 | 2003-07-16 | 4.5 | 3.9 | 118
[12 empty] | 90 | 0.25 | 0.35 | 0.4 | 90 | 0.25 | 0.35 | 0.4 | [5 empty] | August | 20 | 116 | 4.3 | 2.5 | 2003-08-20 | 4.3 | 2.5 | 116
Berryessa Highlands | [11 empty] | 95 | 0.25 | 0.35 | 0.4 | 95 | 0.25 | 0.35 | 0.4 | [5 empty] | September | 17 | 91 | 5.3 | 3.8 | 2003-09-17 | 5.3 | 3.8 | 91
DBP Precursor Removal Compliance Calculations For Water Utility | [11 empty] | 100 | 0.25 | 0.35 | 0.4 | 100 | 0.25 | 0.35 | 0.4 | [5 empty] | October | 15 | 96 | 4 | 3.2 | 2003-10-15 | 4 | 3.2 | 96
Enhanced Coagulation - Year 2 | [11 empty] | 105 | 0.25 | 0.35 | 0.4 | 105 | 0.25 | 0.35 | 0.4 | [5 empty] | November | 19 | 89 | 3.2 | 0.7 | 2003-11-19 | 3.2 | 0.7 | 89
Year: | 2016 | [10 empty] | 110 | 0.25 | 0.35 | 0.4 | 110 | 0.25 | 0.35 | 0.4 | [5 empty] | December | 17 | 64 | 3.8 | 3.6 | 2003-12-17 | 3.8 | 3.6 | 64
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No? | 115 | 0.25 | 0.35 | 0.4 | 115 | 0.25 | 0.35 | 0.4 | [5 empty] | January | 21 | 102 | 11 | 5.1 | 2004-01-21 | 11 | 5.1 | 102
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio |  | 120 | 0.25 | 0.35 | 0.4 | 120 | 0.25 | 0.35 | 0.4 | [5 empty] | February | 18 | 92 | 6.6 | 4.3 | 2004-02-18 | 6.6 | 4.3 | 92
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4 |  | 120.5 | 0.15 | 0.25 | 0.3 | 120.5 | 0.15 | 0.25 | 0.3 | [5 empty] | March
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters) |  | 125 | 0.15 | 0.25 | 0.3 | 125 | 0.15 | 0.25 | 0.3 | [5 empty] | April | 21 | 118 | 8.5 | 2.8 | 2004-04-21 | 8.5 | 2.8 | 118
January | [10 empty] | - | [12 empty] | 0 | May | 19 | 112 | 6.2 | 5.5 | 2004-05-19 | 6.2 | 5.5 | 112
February | [23 empty] | 0 | June | 23 | 126 | 3.8 | 3 | 2004-06-23 | 3.8 | 3 | 126
March | [23 empty] | 0 | July | 21 | 128 | 3 | 2.8 | 2004-07-21 | 3 | 2.8 | 128
April | [10 empty] | - | [12 empty] | 0 | August | 18 | 116 | 4.4 | 3 | 2004-08-18 | 4.4 | 3 | 116
May | [23 empty] | 0 | September | 15 | 132 | 5.6 | 4.2 | 2004-09-15 | 5.6 | 4.2 | 132
June | [23 empty] | 0 | October | 27 | 128 | 6.7 | 2.6 | 2004-10-27 | 6.7 | 2.6 | 128
July | [10 empty] | - | [12 empty] | 0 | November | 17 | 122 | 4.2 | 3 | 2004-11-17 | 4.2 | 3 | 122
August | [23 empty] | 0 | December
September | [23 empty] | 0 | January
October | [10 empty] | - | [12 empty] | 0 | February | 16 | 140 | 10 | 5.2 | 2005-02-16 | 10 | 5.2 | 140
November | [23 empty] | 0 | March | 17 | 100 | 14 | 7.6 | 2005-03-17 | 14 | 7.6 | 100
December | [23 empty] | 0 | April | 22 | 138 | 10 | 5.6 | 2005-04-22 | 10 | 5.6 | 138
[25 empty] | May | 18 | 160 | 6.4 | 5.9 | 2005-05-18 | 6.4 | 5.9 | 160
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter. | [24 empty] | June | 16 | 120 | 5.8 | 3.4 | 2005-06-16 | 5.8 | 3.4 | 120
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than | [24 empty] | July | 14 | 140 | 9.5 | 4.6 | 2005-07-14 | 9.5 | 4.6 | 140
or equal to 1.00, then the system is in compliance with the TOC removal requirements. | [24 empty] | August | 17 | 81 | 3.6 | 3.2 | 2005-08-17 | 3.6 | 3.2 | 81
[25 empty] | September | 22 | 90 | 7.6 | 5.7 | 2005-09-22 | 7.6 | 5.7 | 90
Treated Water TOC Sample Location: |  |  |  | Post Filtration | [20 empty] | October | 19 | 90 | 5.5 | 0.73 | 2005-10-19 | 5.5 | 0.73 | 90
[25 empty] | November | 16 | 80 | 2.98 | 1.08 | 2005-11-16 | 2.98 | 1.08 | 80
Berryessa Highlands | [24 empty] | December | 21 | 89 | 9.2 | 3.7 | 2005-12-21 | 9.2 | 3.7 | 89
DBP Precursor Removal Compliance Calculations For Water Utility | [24 empty] | January | 18 | 65 | 11 | 1.5 | 2006-01-15 | 11 | 1.5 | 35
Enhanced Coagulation - Year 3 | [24 empty] | February | 15 | 110 | 9.2 | 1.7 | 2006-02-15 | 9.2 | 1.7 | 110
Year: | 2017 | [23 empty] | March | 15 | 68 | 5.9 | 1.4 | 2006-03-15 | 5.9 | 1.4 | 68
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No? | [13 empty] | April | 19 | 70 | 14 | 4.1 | 2006-04-18 | 14 | 4.1 | 70
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio | [14 empty] | May | 17 | 120 | 12 | 4.4 | 2006-05-17 | 12 | 4.4 | 120
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4 | [14 empty] | June | 21 | 120 | 5 | 2.2 | 2006-06-19 | 5 | 2.2 | 120
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters) |  |  | >2.0-4.0 | >4.0-8.0 | >8.0 |  | >2.0-4.0 | >4.0-8.0 | >8.0
January | [10 empty] | - | 0 | 0.35 | 0.45 | 0.5 | 0 | 0.35 | 0.45 | 0.5 | 56.82% | 45% | 1.2626 |  | 0
February | [11 empty] | 5 | 0.35 | 0.45 | 0.5 | 5 | 0.35 | 0.45 | 0.5 | 61.7% | 45% | 1.3712 |  | 0
March | [11 empty] | 10 | 0.35 | 0.45 | 0.5 | 10 | 0.35 | 0.45 | 0.5 | 59.32% | 45% | 1.3183 |  | 0
April | [10 empty] | - | 15 | 0.35 | 0.45 | 0.5 | 15 | 0.35 | 0.45 | 0.5 | 58.33% | 45% | 1.2963 |  | 0
May | [11 empty] | 20 | 0.35 | 0.45 | 0.5 | 20 | 0.35 | 0.45 | 0.5 | 54.55% | 45% | 1.2121 |  | 0
June | [11 empty] | 25 | 0.35 | 0.45 | 0.5 | 25 | 0.35 | 0.45 | 0.5 | 44.44% | 45% | 0.98765 |  | 0
July | [10 empty] | - | 30 | 0.35 | 0.45 | 0.5 | 30 | 0.35 | 0.45 | 0.5 | 51.11% | 45% | 1.1358 |  | 0
August | [11 empty] | 35 | 0.35 | 0.45 | 0.5 | 35 | 0.35 | 0.45 | 0.5 | 48.89% | 45% | 1.0864 |  | 0
September | [11 empty] | 40 | 0.35 | 0.45 | 0.5 | 40 | 0.35 | 0.45 | 0.5 | 46.15% | 35% | 1.3187 |  | 0
October | [10 empty] | - | 45 | 0.35 | 0.45 | 0.5 | 45 | 0.35 | 0.45 | 0.5 | 46.51% | 45% | 1.0336 |  | 0
November | [11 empty] | 50 | 0.35 | 0.45 | 0.5 | 50 | 0.35 | 0.45 | 0.5 | 52.17% | 45% | 1.1594 |  | 0
December | [11 empty] | 55 | 0.35 | 0.45 | 0.5 | 55 | 0.35 | 0.45 | 0.5 | 43.9% | 45% | 0.97561 |  | 0
[12 empty] | 60 | 0.35 | 0.45 | 0.5 | 60 | 0.35 | 0.45 | 0.5
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter. | [11 empty] | 60.5 | 0.25 | 0.35 | 0.4 | 60.5 | 0.25 | 0.35 | 0.4
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than | [11 empty] | 65 | 0.25 | 0.35 | 0.4 | 65 | 0.25 | 0.35 | 0.4
or equal to 1.00, then the system is in compliance with the TOC removal requirements. | [11 empty] | 70 | 0.25 | 0.35 | 0.4 | 70 | 0.25 | 0.35 | 0.4
[12 empty] | 75 | 0.25 | 0.35 | 0.4 | 75 | 0.25 | 0.35 | 0.4
Treated Water TOC Sample Location: |  |  |  | Post Filtration | [7 empty] | 80 | 0.25 | 0.35 | 0.4 | 80 | 0.25 | 0.35 | 0.4
[12 empty] | 85 | 0.25 | 0.35 | 0.4 | 85 | 0.25 | 0.35 | 0.4
[12 empty] | 90 | 0.25 | 0.35 | 0.4 | 90 | 0.25 | 0.35 | 0.4
Berryessa Highlands | [11 empty] | 95 | 0.25 | 0.35 | 0.4 | 95 | 0.25 | 0.35 | 0.4
DBP Precursor Removal Compliance Calculations For Water Utility | [11 empty] | 100 | 0.25 | 0.35 | 0.4 | 100 | 0.25 | 0.35 | 0.4
Enhanced Coagulation - Year 4 | [11 empty] | 105 | 0.25 | 0.35 | 0.4 | 105 | 0.25 | 0.35 | 0.4
Year: | 2007 | [10 empty] | 110 | 0.25 | 0.35 | 0.4 | 110 | 0.25 | 0.35 | 0.4
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No? | 115 | 0.25 | 0.35 | 0.4 | 115 | 0.25 | 0.35 | 0.4
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio |  | 120 | 0.25 | 0.35 | 0.4 | 120 | 0.25 | 0.35 | 0.4
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4 |  | 120.5 | 0.15 | 0.25 | 0.3 | 120.5 | 0.15 | 0.25 | 0.3
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters) |  | 125 | 0.15 | 0.25 | 0.3 | 125 | 0.15 | 0.25 | 0.3
January | 16 | 26.5 | 4.4 | 1.9 | Step 1 | 56.82% | 45% | 1.2626 |  |  | Yes | [11 empty] | 1 | 0
February | 14 | 20.5 | 4.7 | 1.8 | Step 1 | 61.7% | 45% | 1.3712 | [14 empty] | 1 | 0
March | 27 | 24.5 | 5.9 | 2.4 | Step 1 | 59.32% | 45% | 1.3183 | 1.3174 | 1.3174 | [12 empty] | 1 | 0
April | 11 | 25 | 4.8 | 2 | Step 1 | 58.33% | 45% | 1.2963 |  |  | Yes | [11 empty] | 1 | 0
May | 9 | 39 | 4.4 | 2 | Step 1 | 54.55% | 45% | 1.2121 | [14 empty] | 1 | 0
June | 13 | 28 | 4.5 | 2.5 | Step 1 | 44.44% | 45% | 0.98765 | 1.1654 | 1.2414 | [12 empty] | 1 | 0
July | 11 | 29.5 | 4.5 | 2.2 | Step 1 | 51.11% | 45% | 1.1358 |  |  | Yes | [11 empty] | 1 | 0
August | 9 | 32.5 | 4.5 | 2.3 | Step 1 | 48.89% | 45% | 1.0864 | [14 empty] | 1 | 0
September | 28 | 30 | 3.9 | 2.1 | Step 1 | 46.15% | 35% | 1.3187 | 1.1803 | 1.221 | [12 empty] | 1 | 0
October | 10 | 31.8 | 4.3 | 2.3 | Step 1 | 46.51% | 45% | 1.0336 |  |  | Yes | [11 empty] | 1 | 0
November | 14 | 42.5 | 4.6 | 2.2 | Step 1 | 52.17% | 45% | 1.1594 | [14 empty] | 1 | 0
December | 20 | 31 | 4.1 | 2.3 | Step 1 | 43.9% | 45% | 0.97561 | 1.0562 | 1.1798 | [12 empty] | 1 | 0
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter.
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than
or equal to 1.00, then the system is in compliance with the TOC removal requirements.
Treated Water TOC Sample Location: |  |  |  | Post Filtration
Berryessa Highlands
DBP Precursor Removal Compliance Calculations For Water Utility
Enhanced Coagulation - Year 5
Year: | 2008
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No?
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters)
January |  |  |  |  | Step 1 | [5 empty] | -
February |  |  |  |  | Step 1
March |  |  |  |  | Step 1
April |  |  |  |  | Step 1 | [5 empty] | -
May |  |  |  |  | Step 1
June |  |  |  |  | Step 1
July |  |  |  |  | Step 1 | [5 empty] | -
August |  |  |  |  | Step 1
September |  |  |  |  | Step 1
October |  |  |  |  | Step 1 | [5 empty] | -
November |  |  |  |  | Step 1
December |  |  |  |  | Step 1
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter.
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than
or equal to 1.00, then the system is in compliance with the TOC removal requirements.
Treated Water TOC Sample Location: |  |  |  | Post Filtration
Berryessa Highlands
DBP Precursor Removal Compliance Calculations For Water Utility
Enhanced Coagulation - Year 6
Year: | 2009
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No?
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters)
January |  |  |  |  | Step 1 | [5 empty] | -
February |  |  |  |  | Step 1
March |  |  |  |  | Step 1
April |  |  |  |  | Step 1 | [5 empty] | -
May |  |  |  |  | Step 1
June |  |  |  |  | Step 1
July |  |  |  |  | Step 1 | [5 empty] | -
August |  |  |  |  | Step 1
September |  |  |  |  | Step 1
October |  |  |  |  | Step 1 | [5 empty] | -
November |  |  |  |  | Step 1
December |  |  |  |  | Step 1
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter.
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than
or equal to 1.00, then the system is in compliance with the TOC removal requirements.
Treated Water TOC Sample Location: |  |  |  | Post Filtration
Berryessa Highlands
DBP Precursor Removal Compliance Calculations For Water Utility
Enhanced Coagulation - Year 7
Year: | 2010
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No?
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters)
January |  |  |  |  | Step 1 | [5 empty] | -
February |  |  |  |  | Step 1
March |  |  |  |  | Step 1
April |  |  |  |  | Step 1 | [5 empty] | -
May |  |  |  |  | Step 1
June |  |  |  |  | Step 1
July |  |  |  |  | Step 1 | [5 empty] | -
August |  |  |  |  | Step 1
September |  |  |  |  | Step 1
October |  |  |  |  | Step 1 | [5 empty] | -
November |  |  |  |  | Step 1
December |  |  |  |  | Step 1
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter.
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than
or equal to 1.00, then the system is in compliance with the TOC removal requirements.
Treated Water TOC Sample Location: |  |  |  | Post Filtration
Berryessa Highlands
DBP Precursor Removal Compliance Calculations For Water Utility
Enhanced Coagulation - Year 8
Year: | 2011
[5 empty] | Basis for Required % Removal | (A) | (B) | (C) | (D)a | (E)b | In Compliance Yes/No?
|  | Source Water |  | Treated |  | Actual | Required | Removal | Quarterly | RAA Ratio
Month | Day | Alk | TOC | Water TOC |  | % TOC | % TOC | Ratio | Average | (Last 4
|  | (mg/L) | (mg/L) | (mg/L) |  | Removal | Removal | (A) / (B) | Ratio | Ouarters)
January |  |  |  |  | Step 1 | [5 empty] | -
February |  |  |  |  | Step 1
March |  |  |  |  | Step 1
April |  |  |  |  | Step 1 | [5 empty] | -
May |  |  |  |  | Step 1
June |  |  |  |  | Step 1
July |  |  |  |  | Step 1 | [5 empty] | -
August |  |  |  |  | Step 1
September |  |  |  |  | Step 1
October |  |  |  |  | Step 1 | [5 empty] | -
November |  |  |  |  | Step 1
December |  |  |  |  | Step 1
a Quarterly ratio calculated as an average of the actual / required % removal ratio for the three months in that quarter.
b Running Annual Average (RAA) of quarterly TOC % removal ratios for the last four quarters; if the results in column (E) is greater than
or equal to 1.00, then the system is in compliance with the TOC removal requirements.
Treated Water TOC Sample Location: |  |  |  | Post Filtration
Note on E9: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on E37: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on E64: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on E92: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on B4: Type in system name here:
Note on G8: Type in Step 1 or Step 2 for each month.
Note on H8: Automatically calculated.
Note on I8: Automatically determined.
Note on J8: Automatically calculated.
Note on K8: Automatically calculated.
Note on L8: Automatically calculated.
Note on G36: Type in Step 1 or Step 2 for each month.
Note on H36: Automatically calculated.
Note on I36: Automatically determined.
Note on J36: Automatically calculated.
Note on K36: Automatically calculated.
Note on L36: Automatically calculated.
Note on G63: Type in Step 1 or Step 2 for each month.
Note on H63: Automatically calculated.
Note on I63: Automatically determined.
Note on J63: Automatically calculated.
Note on K63: Automatically calculated.
Note on L63: Automatically calculated.
Note on G91: Type in Step 1 or Step 2 for each month.
Note on H91: Automatically calculated.
Note on I91: Automatically determined.
Note on J91: Automatically calculated.
Note on K91: Automatically calculated.
Note on L91: Automatically calculated.
Note on M8: Automatically Determined.
Note on M36: Automatically Determined.
Note on M63: Automatically Determined.
Note on M91: Automatically Determined.
Note on AP9: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on G118: Type in Step 1 or Step 2 for each month.
Note on H118: Automatically calculated.
Note on I118: Automatically determined.
Note on J118: Automatically calculated.
Note on K118: Automatically calculated.
Note on L118: Automatically calculated.
Note on M118: Automatically Determined.
Note on E119: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on G145: Type in Step 1 or Step 2 for each month.
Note on H145: Automatically calculated.
Note on I145: Automatically determined.
Note on J145: Automatically calculated.
Note on K145: Automatically calculated.
Note on L145: Automatically calculated.
Note on M145: Automatically Determined.
Note on E146: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on G172: Type in Step 1 or Step 2 for each month.
Note on H172: Automatically calculated.
Note on I172: Automatically determined.
Note on J172: Automatically calculated.
Note on K172: Automatically calculated.
Note on L172: Automatically calculated.
Note on M172: Automatically Determined.
Note on E173: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.
Note on G199: Type in Step 1 or Step 2 for each month.
Note on H199: Automatically calculated.
Note on I199: Automatically determined.
Note on J199: Automatically calculated.
Note on K199: Automatically calculated.
Note on L199: Automatically calculated.
Note on M199: Automatically Determined.
Note on E200: Source Water: Samples for alkalinity and TOC must be taken of the raw water before any chemical treatment.

## TOC-Reg
TOC Regulation Requirements
Section 64536
Alternatives to Enhanced Coagulation Performance Requirements
For Plants Using Conventional Treatment:
Must meet one of the following:
TOC (source or treated) < 2.0 mg/L
TOC (source) < 4.0 mg/L, alkalinity (source) > 60 mg/L, and TTHM <= 0.040 mg/L and
HAA5 <= 0.030 mg/L
TTHM <= 0.040 mg/L, HAA5 <= 0.030 mg/L and only chorine used as primary and residual disinfectant
SUVA (source or treated < 2.0 L/mg-m (calculated as UV254/DOC not TOC)
Results are calculated quarterly as a running annual average.
If the water system can not meet any one of the alternative compliance criteria above, then they
must comply with the requirements in Section 64536.2.
Section 64536.2
Required Removal of TOC by Enhanced Coagulation
For Plants Using Conventional Treatment:
Step 1 Removal Percentages
Table 64536.2-A
SOURCE WATER TOC (mg/L) | SOURCE WATER ALKALINITY (mg/L as CaCO3)
| 0 to 60 | >60 to 120 | >120
>2.0 - 4.0 | 35% | 25% | 15%
>4.0 - 8.0 | 45% | 35% | 25%
>8.0 | 50% | 40% | 30%
Source water TOC and/or alkalinity may change requiring different TOC removal requirement.
Section 64536.4(b): In any month that one or more of the conditions below are met, the system may
assign a monthly removal TOC ratio of 1.0 (in lieu of the calculated value):
TOC (source or treated) <= 2.0 mg/L
SUVA (source or treated <= 2.0 L/mg-m (calculated as UV254/DOC not TOC)
Step 2 Alternative TOC Removal Requirements
For Plants Using Conventional Treatment &
Can Not Meet: Alternative Compliance Criteria (Section 64536) or
Step 1 (Section 64536.2)
Must conduct the following (Section 64536.2d(1)(2)(3)(4)):
Conduct bench or pilot scale testing to establish an alternative TOC removal requirement
Determine incremental removal of TOC for each 10 mg/L of alum (or equivalent ferric salt) added
When slope is < 0.3 TOC mg/L per 10 mg/L of alum added, then percent TOC removed at this
point is the new compliance requirement (this is called the point of diminishing return (PODR)
Systems are required to submit an application to DHS for approval of Step 2 TOC removal requirement.
Target pH under Step 2 Requirements (jar testing)
Table 64536.2-B
| Alkalinity (mg/L as CaCO3) | Target pH
| 0 - 60 | 5.5
| > 60 - 120 | 6.3
| > 120 - 240 | 7
| > 240 | 7.5
The Step 2 procedure requires that incremental coagulant addition be continued until the pH of the tested
sample is at or below the "target pH" to ensure that the treatability of the sample is examined over a range
of pH values.
It is possible that the PODR is met twice. If this happens, use the second PODR for determining the
percent TOC removed for new compliance.

## TTHM & HAA5 Plan3
[12 empty] | TTHM | TTHM | TTHM | TTHM | TTHM |  |  | HAA5 | HAA5 | HAA5 | HAA5 | HAA5
Berryessa Highlands | [11 empty] | Site 1 | Site 2 | Site 3 | Site 4 |  |  |  | Site 1 | Site 2 | Site 3 | Site 4
TTHM and HAA5 Monitoring Report 2004 | [10 empty] | 2002-03-01 | 0.04 | 0.056 | 0.063 | 0.065 | 0.08 |  | 2002-03-01 | 0.029 | 0.038 | 0.024 | 0.021 | 0.06
Year 1 | [10 empty] | 2002-06-01 | 0.041 | 0.058 | 0.052 | 0.051 | 0.08 |  | 2002-06-01 | 0.021 | 0.037 | 0.032 | 0.033 | 0.06
| Year: | 2015 | [8 empty] | 2002-09-01 | 0.053 | 0.059 | 0.056 | 0.054 | 0.08 |  | 2002-09-01 | 0.023 | 0.011 | 0.019 | 0.019 | 0.06
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No? | 2002-12-01 | 0.048 | 0.057 | 0.034 | 0.036 | 0.08 | 0.051 | 2002-12-01 | 0.031 | 0.03 | 0.027 | 0.036 | 0.06 | 0.027
| Month | Day |  | Sites | [6 empty] | 2003-03-01 | 0.105 | 0.137 | 0.097 | 0.098 | 0.08 | 0.065 | 2003-03-01 | 0.04 | 0.032 | 0.046 | 0.042 | 0.06 | 0.03
|  |  | Test | 1 | 2 | 3 | 4 |  |  |  | 2003-06-01 | 0.034 | 0.056 | 0.045 | 0.047 | 0.08 | 0.064 | 2003-06-01 | 0.016 | 0.01 | 0.01 | 0.014 | 0.06 | 0.025
1 | [7 empty] | - | - |  | 2003-09-01 | 0.04 | 0.059 | 0.052 | 0.052 | 0.08 | 0.062 | 2003-09-01 | 0.055 | 0.042 | 0.045 | 0.044 | 0.06 | 0.032
[8 empty] | - |  |  | 2003-12-01 | 0.026 | 0.038 | 0.03 | 0.031 | 0.08 | 0.059 | 2003-12-01 | 0.033 | 0.03 | 0.032 | 0.033 | 0.06 | 0.033
2 | [7 empty] | - | - |  | 2004-03-01 | 0.053 | 0.061 | 0.05 | 0.048 | 0.08 | 0.045 | 2004-03-01 | 0.031 | 0.032 | 0.029 | 0.03 | 0.06 | 0.03
[8 empty] | - |  |  | 2004-06-01 | 0.037 | 0.061 | 0.052 | 0.055 | 0.08 | 0.047 | 2004-06-01 | 0.051 | 0.03 | 0.013 | 0.008 | 0.06 | 0.034
3 | [7 empty] | - | - |  | 2004-09-01 | 0.04 | 0.059 | 0.052 | 0.052 | 0.08 | 0.047 | 2004-09-01 | 0.053 | 0.042 | 0.045 | 0.044 | 0.06 | 0.034
[8 empty] | - |  |  | 2004-12-01 | 0.067 | 0.088 | 0.073 | 0.066 | 0.08 | 0.057 | 2004-12-01 | 0.065 | 0.031 | 0.032 | 0.042 | 0.06 | 0.036
4 | [7 empty] | - | - | - | 2005-03-01 | 0.157 | 0.147 | 0.139 | 0.144 | 0.08 | 0.0805 | 2005-03-01 | 0.024 | 0.024 | 0.036 | 0.037 | 0.06 | 0.036
[8 empty] | - | - |  | 2005-06-01 | 0.1156 | 0.1139 | 0.0985 | 0.1019 | 0.08 | 0.0946 | 2005-06-01 | 0.022 | 0.01496 | 0.01736 | 0.02085 | 0.06 | 0.034
[11 empty] | 2005-09-01 | 0.035 | 0.042 | 0.036 | 0.04 | 0.08 | 0.091 | 2005-09-01 | 0.023 | 0.01 | 0.021 | 0.017 | 0.06 | 0.027
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1) | [7 empty] | 2005-12-01 | 0.0834 | 0.029 | 0.027 | 0.026 | 0.08 | 0.083 | 2005-12-01 | 0.033 | 0.008 | 0.015 | 0.009 | 0.06 | 0.021
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1) | [7 empty] | 2006-03-01 | 0.155 | 0.133 | 0.101 | 0.104 | 0.08 | 0.078 | 2006-03-01 | 0.017 | 0.05 | 0.035 | 0.036 | 0.06 | 0.022
|  | 3. | Pratt Ave. (Mean Residence time zone 1) | [7 empty] | 2006-06-01 | 0.068 | 0.079 | 0.034 | 0.073 | 0.08 | 0.067 | 2006-06-01 | 0.036 | 0.039 | 0.028 | 0.037 | 0.06 | 0.026
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average | [6 empty] | min: | 0.026 |  |  |  | 0.045 |  | min: | 0.008 |  |  |  | 0.021
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average | [6 empty] | Max: | 0.157 |  |  |  | 0.0946 |  | Max: | 0.065 |  |  |  | 0.036
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2005
Year 2
| Year: | 2016
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | [7 empty] | - | - | -
[8 empty] | - | -
2 | [7 empty] | - | - | -
[8 empty] | - | -
3 | [7 empty] | - | - | -
[8 empty] | - | -
4 | [7 empty] | - | - | -
[8 empty] | - | -
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2006
Year 3
| Year: | 2017
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | February | 17 | TTHM | 0.063 | 0.032 | 0.052 | 0.0063 | 0.038325 |  | Yes
|  |  | HAA5 | 0.013 | 0.036 | 0.07 | 0.0078 | 0.0317
2 | May | 19 | TTHM | 0.046 | 0.055 | 0.047 | 0.051 | 0.04975 |  | Yes
|  |  | HAA5 | 0.017 | 0.056 | 0.059 | 0.052 | 0.046
3 | August | 16 | TTHM | 0.056 | 0.082 | 0.05 | 0.054 | 0.0605 |  | Yes
|  |  | HAA5 | 0.014 | 0.058 | 0.049 | 0.049 | 0.0425
4 | November | 15 | TTHM | 0.046 | 0.052 | 0.042 | 0.046 | 0.0465 | 0.048769 | Yes
|  |  | HAA5 | 0.012 | 0.047 | 0.048 | 0.048 | 0.03875 | 0.039738
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2007
Year 4
| Year: | 2018
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | February | 14 | TTHM | 0.039 | 0.051 | 0.046 | 0.047 | 0.04575 | 0.050625 | Yes
|  |  | HAA5 | 0.005 | 0.048 | 0.046 | 0.044 | 0.03575 | 0.04075
2 | May | 16 | TTHM | 0.047 | 0.072 | 0.049 | 0.052 | 0.055 | 0.051937 | Yes
|  |  | HAA5 | 0.025 | 0.067 | 0.056 | 0.058 | 0.0515 | 0.042125
3 | August | 15 | TTHM | 0.061 | 0.09 | 0.074 | 0.076 | 0.07525 | 0.055625 | Yes
|  |  | HAA5 | 0.0159 | 0.0914 | 0.0826 | 0.0822 | 0.068025 | 0.048506
4 | November | 15 | TTHM | 0.058 | 0.06 | 0.064 | 0.049 | 0.05775 | 0.058437 | Yes
|  |  | HAA5 | 0.024 | 0.052 | 0.061 | 0.045 | 0.0455 | 0.050194
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2008
Year 5
| Year: | 2019
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | [7 empty] | - | - | -
[8 empty] | - | -
2 | [7 empty] | - | - | -
[8 empty] | - | -
3 | [7 empty] | - | - | -
[8 empty] | - | -
4 | [7 empty] | - | - | -
[8 empty] | - | -
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2009
Year 6
| Year: | 2020
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | March |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
2 | June |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
3 | September |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
4 | December |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2010
Year 7
| Year: | 2021
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | March |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
2 | June |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
3 | September |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
4 | December |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Berryessa Highlands
TTHM and HAA5 Monitoring Report 2011
Year 8
| Year: | 2022
Qrt. | [7 empty] | Quarterly Average | Running Annual Average (Last 4 Quarters) | In Compliance Yes/No?
| Month | Day |  | Sites
|  |  | Test | 1 | 2 | 3 | 4
1 | March |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
2 | June |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
3 | September |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
4 | December |  | TTHM |  |  |  |  | - | - | -
|  |  | HAA5 |  |  |  |  | - | -
| Sites: | 1. | Niebaum Ln. @Church (Max. Residence time southeast zone 1)
|  | 2. | 3029 St. Helena Hwy. (Max. Residence time northwest zone1)
|  | 3. | Pratt Ave. (Mean Residence time zone 1)
|  | 4. | 1240 Oak St. (Mean Residence time zone1)
|  |  | Total Trihalomethanes (TTHM): | 0.08 | mg/L, MCL based on running annual average
|  |  | Five Haloacetic Acids (HAA5): | 0.06 | mg/L, MCL based on running annual average
Note on C9: Month: Enter month of quarter that sample set was taken.
Note on C33: Month: Enter month of quarter that sample set was taken.
Note on C20: Sites: Enter name and/or address of sample site(s).
Note on C44: Sites: Enter name and/or address of sample site(s).
Note on C57: Month: Enter month of quarter that sample set was taken.
Note on C81: Month: Enter month of quarter that sample set was taken.
Note on C68: Sites: Enter name and/or address of sample site(s).
Note on C92: Sites: Enter name and/or address of sample site(s).
Note on B4: Type in system name here:
Note on J8: Automatically Calculated.
Note on K8: Automatically Determined.
Note on J32: Automatically Calculated.
Note on K32: Automatically Determined.
Note on J56: Automatically Calculated.
Note on K56: Automatically Determined.
Note on J80: Automatically Calculated.
Note on K80: Automatically Determined.
Note on L8: Automatically Determined.
Note on L56: Automatically Determined.
Note on L80: Automatically Determined.
Note on L32: Automatically Determined.
Note on J104: Automatically Calculated.
Note on K104: Automatically Determined.
Note on L104: Automatically Determined.
Note on C105: Month: Enter month of quarter that sample set was taken.
Note on C116: Sites: Enter name and/or address of sample site(s).
Note on J128: Automatically Calculated.
Note on K128: Automatically Determined.
Note on L128: Automatically Determined.
Note on C129: Month: Enter month of quarter that sample set was taken.
Note on C140: Sites: Enter name and/or address of sample site(s).
Note on J152: Automatically Calculated.
Note on K152: Automatically Determined.
Note on L152: Automatically Determined.
Note on C153: Month: Enter month of quarter that sample set was taken.
Note on C164: Sites: Enter name and/or address of sample site(s).
Note on J176: Automatically Calculated.
Note on K176: Automatically Determined.
Note on L176: Automatically Determined.
Note on C177: Month: Enter month of quarter that sample set was taken.
Note on C188: Sites: Enter name and/or address of sample site(s).

## Chlorine
City of St. Helena
Chlorine Monitoring Report
| Year 1, 2015 |  |  |  | Year 2, 2016
Month | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No? | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No?
January | [7 empty] | -
February
March |  |  | - |  |  |  | -
April | [7 empty] | -
May
June |  |  | - |  |  |  | -
July | [7 empty] | -
August
September |  |  | - |  |  |  | -
October |  |  |  | - |  |  |  | -
November
December |  |  | - |  |  |  | -
| Year 3, 2017 |  |  |  | Year 4, 2018
Month | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No? | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No?
January |  |  |  | - |  |  |  | -
February
March |  |  | - |  |  |  | -
April |  |  |  | - |  |  |  | -
May
June |  |  | - |  |  |  | -
July |  |  |  | - |  |  |  | -
August
September |  |  | - |  |  |  | -
October |  |  |  | - |  |  |  | -
November
December |  |  | - |  |  |  | -
| Year 5, 2019 |  |  |  | Year 6, 2020
Month | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No? | # of Samples | Avg. Cl2 mg/L | RAA (Last 12 months) | MRDL Violated Yes/No?
January |  |  |  | - |  |  |  | -
February
March |  |  | - |  |  |  | -
April |  |  |  | - |  |  |  | -
May
June |  |  | - |  |  |  | -
July |  |  |  | - |  |  |  | -
August
September |  |  | - |  |  |  | -
October |  |  |  | - |  |  |  | -
November
December |  |  | - |  |  |  | -
| Chlorine Residual: | 4 | mg/L, MRDL based on running annual average (RAA)
Note on B3: Type in system name here:
Note on F7: Automatically Determined.
Note on J7: Automatically Determined.
Note on F25: Automatically Determined.
Note on J25: Automatically Determined.
Note on F43: Automatically Determined.
Note on J43: Automatically Determined.

## Bromate (hidden)
Highlands Water Company
Bromate Monitoring Report
| Year 1, 2004 |  |  |  |  | Year 2, 2005
Month | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No? | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No?
January | 13 | 0.01 | 0.0066667 |  |  | 11 | 0.005 | 0.005 |  | No
February | 10 | 0.005 |  |  |  | 8 | 0.005
March | 9 | 0.005 |  |  |  | 8 | 0.005
|  |  |  | - |  |  |  |  | 0.005
April | 13 | 0.005 | 0.005 |  |  | 12 | 0.005 | 0.005 |  | No
May | 11 | 0.005 |  |  |  | 10 | 0.005
June | 8 | 0.005 |  |  |  | 8 | 0.005
|  |  |  | - |  |  |  |  | 0.005
July | 14 | 0.005 | 0.005 |  |  | 8 | 0.005 | 0.005 |  | No
August | 10 | 0.005 |  |  |  | 10 | 0.005
September | 21 | 0.005 |  |  |  | 15 | 0.005
|  |  |  | - |  |  |  |  | 0.005
October | 10 | 0.005 | 0.005 |  | No | 4 | 0.005 | 0.005 |  | No
November | 16 | 0.005 |  |  |  | 9 | 0.005
December | 12 | 0.005 |  |  |  | 7 | 0.005
|  |  |  | 0.0054167 |  |  |  |  | 0.005
| Bromate MCL: | 0.01 | mg/L, based on running annual average (RAA)
| Sample Location: | Entry into distribution system after clearwell
Highlands Water Company
Bromate Monitoring Report
| Year 3, 2006 |  |  |  |  | Year 4, 2007
Month | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No? | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No?
January | 10 | 5e-05 | 5e-05 |  | No | 9 | 5e-06 | 3.7333e-06 |  | No
February | 15 | 5e-05 |  |  |  | 13 | 5e-06
March | 15 | 5e-05 |  |  |  | 13 | 1.2e-06
|  |  |  | 0.0037625 |  |  |  |  | 1.6775e-05
April | 11 | 5e-05 | 5e-05 |  | No | 20 | 1e-08 | 6.7e-07 |  | No
May | 10 | 5e-05 |  |  |  | 8 | 1e-06
June | 13 | 5e-05 |  |  |  | 14 | 1e-06
|  |  |  | 0.002525 |  |  |  |  | 4.4425e-06
July | 11 | 5e-06 | 1.1667e-05 |  | No |  |  | 1.7e-05 |  | No
[6 empty] | 11 | 1e-06
August | 8 | 3e-05
[6 empty] | 14 | 5e-05
September | 13 | 0
|  |  |  | 0.0012779 |  | 13 | 0 |  | 5.7758e-06
October | 11 | 0 | 1.7e-06 |  | No | 9 | 0 | - |  | -
November | 14 | 1e-07 |  |  |  | 14 | 0
December | 12 | 5e-06
|  |  |  | 2.8342e-05 |  |  |  |  | -
| Bromate MCL: | 0.01 | mg/L, based on running annual average (RAA)
| Sample Location: | Entry into distribution system after clearwell
Highlands Water Company
Bromate Monitoring Report
| Year 5, 2008 |  |  |  |  | Year 6, 2009
Month | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No? | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No?
January |  |  | - |  | - |  |  | - |  | -
February
March
|  |  |  | - |  |  |  |  | -
April |  |  | - |  | - |  |  | - |  | -
May
June
|  |  |  | - |  |  |  |  | -
July |  |  | - |  | - |  |  | - |  | -
August
September
|  |  |  | - |  |  |  |  | -
October |  |  | - |  | - |  |  | - |  | -
November
December
|  |  |  | - |  |  |  |  | -
| Bromate MCL: | 0.01 | mg/L, based on running annual average (RAA)
| Sample Location: | Entry into distribution system after clearwell
Highlands Water Company
Bromate Monitoring Report
| Year 7, 2010 |  |  |  |  | Year 8, 2011
Month | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No? | Day | BrO3 mg/L | Quarterly Average | RAA (Last 12 months) | MCL Violated Yes/No?
January |  |  | - |  | - |  |  | - |  | -
February
March
|  |  |  | - |  |  |  |  | -
April |  |  | - |  | - |  |  | - |  | -
May
June
|  |  |  | - |  |  |  |  | -
July |  |  | - |  | - |  |  | - |  | -
August
September
|  |  |  | - |  |  |  |  | -
October |  |  | - |  | - |  |  | - |  | -
November
December
|  |  |  | - |  |  |  |  | -
| Bromate MCL: | 0.01 | mg/L, based on running annual average (RAA)
| Sample Location: | Entry into distribution system after clearwell
Note on B3: Type in Name of Water System Here:
Note on E7: Automatically Calculated.
Note on F7: Automatically Calculated.
Note on G7: Automatically Determined.
Note on J7: Automatically Calculated.
Note on K7: Automatically Calculated.
Note on L7: Automatically Determined.
Note on E42: Automatically Calculated.
Note on F42: Automatically Calculated.
Note on G42: Automatically Determined.
Note on J42: Automatically Calculated.
Note on K42: Automatically Calculated.
Note on L42: Automatically Determined.
Note on E77: Automatically Calculated.
Note on F77: Automatically Calculated.
Note on G77: Automatically Determined.
Note on J77: Automatically Calculated.
Note on K77: Automatically Calculated.
Note on L77: Automatically Determined.
Note on E112: Automatically Calculated.
Note on F112: Automatically Calculated.
Note on G112: Automatically Determined.
Note on J112: Automatically Calculated.
Note on K112: Automatically Calculated.
Note on L112: Automatically Determined.

## Analytical Methods
Analytical Methods
Systems must use the analytical methods specified in regulations.
Approved analytical methods are listed in the table below:
EPA Approved Analytical Methods
Constituent | Method
TTHM1 | EPA 502.2 EPA 524.2 EPA 551.1
HAA51 | EPA 552.1 EPA 552.2 Standard Method (SM) 6251 B
TOC1,2 | SM 5310 B - Combustion-Infrared SM 5310 C - Persulfate-Ultraviolet Oxidation SM 5310 D - Wet Oxidation
Free Chlorine Chloramines | SM 4500-Cl D - Amperometric Titration SM 4500-Cl F - DPD Ferrous Titrimetric SM 4500-Cl G - DPD Colorimetric SM 4500-Cl H - Syringaldazine (FACTS)
Total Chlorine | SM 4500-Cl E - Low Level Amperometric Titration SM 4500-Cl I - Iodometric Electrode Technique
Bromate1 | EPA 300.1 - Ion Chromatography
1Analyses must be performed by a lab certified by the State or the EPA 2Federal DPBR (40 CFR Part 141.131 (a) (2)) -TOC methods are from the supplement to the 19th edition of Standard Methods. TOC methods from the 19th edition and earlier/later editions of Standard Methods are not the approved methods.