## Slide 1: Clearlake Oaks CWD CA1710001 Lake County Jar Test
by Guy Schott, P.E.
June 16, 2020

## Slide 2: Clearlake Oaks CWD Source Water: Clear Lake Conventional Treatment

## Slide 3: Conventional Treatment Plant

## Slide 4: Clearlake Oaks CWD.: Source Water Characteristics June 16, 2020
Source
Post Ozone Sample
pH: 8.41
Turbidity: 3.03 NTU
UVT: 89.0%
UVA: 0.050/cm
0.4 um Filtered
Turbidity: 0.26 NTU
UVT: 91.6%
UVA: 0.038/cm
Plant Filtrate
Coagulant Dose: 28 mg/L 9800
Turbidity: 0.10 NTU
UVT: 95.4%
UVA: 0.020/cm
UVA Reduction: 47.4%
GAC Filtrate
Turbidity: 0.07 NTU
UVT: 96.4%
UVA: 0.015/cm
UVA Reduction: 60.5%

## Slide 5: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 6: Applied Coagulants for Jar Testing
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
83% Basicity
SG = 1.34
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
20% Trade Secret
35-45% Water
SG = 1.25-1.34
Pro Pac 9810 (NTU Technologies)
45% Aluminum Chlorohydrate
5% Trade Secret
45% Water
SG = 1.25-1.34
Advanced Coagulant
12.55% Al2O3
6.64% Al
66.4% Basicity
SG = 1.3

## Slide 7: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 8.41
LCA #1:
9800: 24.9 mg/L as product
pH adjusted to 7.5 w/acetic acid solution
LCA #2:
Advance Coagulant: 102 mg/L as product
pH adjusted to 7.5 w/acetic acid solution
LCA #3:
9810: Manually added 7 mg/L as product
9800: 14.5 mg/L as product
pH adjusted to 7.5 w/acetic acid solution

## Slide 8: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength). Alum Sulfate is reported as Alum.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 9: Clearlake Oaks CWS: Jar Test 1-4 Results Post-Ozone Source Water
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration min | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 30 | 5 | 24 | 0.18 | 93.8 | 0.028 | 26.3 | 0.92
J2 | 30 | 5 | 26 | 0.12 | 94.6 | 0.024 | 36.8 | 0.52
J3 | 30 | 5 | 28 | 0.11 | 94.2 | 0.025 | 34.2 | 0.46
J4 | 30 | 5 | 30 | 0.11 | 94.6 | 0.023 | 39.5 | 0.41

## Slide 10: Clearlake Oaks CWS: Jar Test 5-8 Results Post-Ozone Source Water
Jar # | 200 RPM Flash Mix sec | 30 RPM Floc Duration min | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J5 | 30 | 5 | 28 | 0.07 | 95.1 | 0.021 | 44.7 | 0.50
J6 | 30 | 5 | 30 | 0.08 | 95.0 | 0.022 | 42.1 | 0.52
J7 | 30 | 5 | 32 | 0.06 | 94.2 | 0.025 | 34.2 | 0.42
J8 | 30 | 5 | 34 | 0.09 | 95.1 | 0.021 | 44.7 | 0.42

## Slide 11: Clearlake Oaks CWS: Jar Test 9-10 Results Post-Ozone Source Water, Flash Mix (200 RPM, 30 sec)
Jar # | 30 RPM Floc Duration minutes | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 5 | 28 | 0.13 | 94.2 | 0.025 | 34.2 | 0.35
J10 | 5 | 30 | 0.11 | 94.3 | 0.025 | 34.2 | 0.32

## Slide 12: Clearlake Oaks CWS: Jar Test 11-16 Results Post-Ozone Source Water, Flash Mix (200 RPM, 30 sec)
Jar # | 30 RPM Floc Duration minutes | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J11 | 5 | 21 | 7.0 | 0.11 | 93.9 | 0.027 | 28.9 | 0.40
J12 | 5 | 22.5 | 7.5 | 0.09 | 94.3 | 0.025 | 34.2 | 0.31
J13 | 5 | 22 | 0 | 0.15 | 93.9 | 0.027 | 28.9 | 0.48
J14 | 5 | 24 | 0 | 0.12 | 93.8 | 0.027 | 28.9 | 0.53
J15 | 5 | 26 | 0 | 0.11 | 93.7 | 0.028 | 26.3 | 0.48
J16 | 5 | 28 | 0 | 0.11 | 93.7 | 0.027 | 28.9 | 0.43

## Slide 13: Clearlake Oaks CWS: Jar Test 17-20 Results Post-Ozone Source Water, Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Duration minutes | Adv Coag. mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 5 | 70 | 0.15 | 93.7 | 0.028 | 26.3 | 0.40
J18 | 5 | 80 | 0.12 | 93.9 | 0.027 | 28.9 | 0.40
J19 | 5 | 90 | 0.11 | 94.2 | 0.026 | 31.6 | 0.35
J20 | 5 | 100 | 0.08 | 94.4 | 0.025 | 34.2 | 0.29

## Slide 14: Clearlake Oaks CWS: Jar Test 21-24 Results Post-Ozone Source Water, Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Duration minutes | 9800 mg/L | NaOCl mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 5 | 26 | 0 | 0.09 | 94.2 | 0.025 | 34.2 | 0.25
J22 | 5 | 28 | 0 | 0.08 | 94.2 | 0.025 | 34.2 | 0.28
J23 | 5 | 26 | 1.0 | 0.10 | 93.1 | 0.031 | 18.4 | 0.32
J24 | 5 | 28 | 1.0 | 0.08 | 93.2 | 0.030 | 21.1 | 0.29

## Slide 15: Clearlake Oaks CWS: Jar Test 25-28 Results Post-Ozone Source Water, Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Duration minutes | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 5 | 22 | 2.2 | 0.12 | 93.9 | 0.027 | 28.9 | 0.33
J26 | 5 | 24 | 2.4 | 0.08 | 94.0 | 0.026 | 31.6 | 0.30
J27 | 5 | 26 | 2.6 | 0.09 | 94.0 | 0.026 | 31.6 | 0.31
J28 | 5 | 28 | 2.8 | 0.12 | 94.3 | 0.025 | 34.2 | 0.33

## Slide 16: Clearlake Oaks CWS: Jar Test 29-36 Results Post-Ozone Source Water, Flash Mix 200 RPM (30 sec)
Jar # | 30 RPM Floc Duration minutes | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J29 | 5 | 26 | 0.10 | 94.6 | 0.024 | 36.8 | 0.31
J30 | 5 | 28 | 0.09 | 94.5 | 0.024 | 36.8 | 0.35
J31 | 5 | 30 | 0.09 | 94.3 | 0.025 | 34.2 | 0.32
J32 | 5 | 32 | 0.09 | 94.6 | 0.024 | 36.8 | 0.30
J33 | 5 | 22 | 0.11 | 94.2 | 0.025 | 34.2 | 0.47
J34 | 5 | 24 | 0.09 | 94.2 | 0.025 | 34.2 | 0.34
J35 | 5 | 26 | 0.09 | 94.5 | 0.024 | 36.8 | 0.32
J36 | 5 | 34 | 0.09 | 94.7 | 0.023 | 39.5 | 0.25

## Slide 17: Jars 1-4 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 18: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
24 mg/L 9800
Filtrate 0.18 NTU
UVT: 93.8%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.92 NTU
26 mg/L 9800
Filtrate 0.12 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.52 NTU
28 mg/L 9800
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.024/cm
UVA Reduction: 34.2%
Settled: 0.46 NTU
30 mg/L 9800
Filtrate 0.11 NTU
UVT: 94.6%
UVA: 0.023/cm
UVA Reduction: 39.5%
Settled: 0.41 NTU

## Slide 19: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
24 mg/L 9800
Filtrate 0.18 NTU
UVT: 93.8%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.92 NTU
26 mg/L 9800
Filtrate 0.12 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.52 NTU
28 mg/L 9800
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.024/cm
UVA Reduction: 34.2%
Settled: 0.46 NTU
30 mg/L 9800
Filtrate 0.11 NTU
UVT: 94.6%
UVA: 0.023/cm
UVA Reduction: 39.5%
Settled: 0.41 NTU

## Slide 20: Jars 5-8 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 21: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
28 mg/L 9810
Filtrate 0.07 NTU
UVT: 95.1%
UVA: 0.021/cm
UVA Reduction: 44.7%
Settled: 0.50 NTU
30 mg/L 9810
Filtrate 0.08 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction: 42.1%
Settled: 0.52 NTU
32 mg/L 9810
Filtrate 0.06 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.42 NTU
34 mg/L 9810
Filtrate 0.09 NTU
UVT: 95.1%
UVA: 0.021/cm
UVA Reduction: 44.7%
Settled: 0.42 NTU

## Slide 22: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
28 mg/L 9810
Filtrate 0.07 NTU
UVT: 95.1%
UVA: 0.021/cm
UVA Reduction: 44.7%
Settled: 0.50 NTU
30 mg/L 9810
Filtrate 0.08 NTU
UVT: 95.0%
UVA: 0.022/cm
UVA Reduction: 42.1%
Settled: 0.52 NTU
32 mg/L 9810
Filtrate 0.06 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.42 NTU
34 mg/L 9810
Filtrate 0.09 NTU
UVT: 95.1%
UVA: 0.021/cm
UVA Reduction: 44.7%
Settled: 0.42 NTU

## Slide 24: Jars 9-12 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9810/9890

## Slide 25: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.35 NTU
30 mg/L 9810
Filtrate 0.11 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.32 NTU
21 mg/L 9800
7 mg/L 9890
Filtrate 0.11 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.40 NTU
22.5 mg/L 9800
7.5 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.31 NTU

## Slide 26: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
28 mg/L 9810
Filtrate 0.13 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.35 NTU
30 mg/L 9810
Filtrate 0.11 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.32 NTU
21 mg/L 9800
7 mg/L 9890
Filtrate 0.11 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.40 NTU
22.5 mg/L 9800
7.5 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.31 NTU

## Slide 28: Jars 13-16 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 29: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
22 mg/L 9800
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.48 NTU
24 mg/L 9800
Filtrate 0.12 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.53 NTU
26 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.48 NTU
28 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.7%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.43 NTU

## Slide 30: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
22 mg/L 9800
Filtrate 0.15 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.48 NTU
24 mg/L 9800
Filtrate 0.12 NTU
UVT: 93.8%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.53 NTU
26 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.48 NTU
28 mg/L 9800
Filtrate 0.11 NTU
UVT: 93.7%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.43 NTU

## Slide 32: Jars 17-20 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant Advanced Coagulant

## Slide 33: Jars 17-20: End of 5-minute flocculation (30 RPM) duration.
70 mg/L Adv Coag
Filtrate 0.15 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.40 NTU
80 mg/L Adv Coag
Filtrate 0.12 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.40 NTU
90 mg/L Adv Coag
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.35 NTU
100 mg/L Adv Coag
Filtrate 0.08 NTU
UVT: 94.4%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.29 NTU

## Slide 34: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
70 mg/L Adv Coag
Filtrate 0.15 NTU
UVT: 93.7%
UVA: 0.028/cm
UVA Reduction: 26.3%
Settled: 0.40 NTU
80 mg/L Adv Coag
Filtrate 0.12 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.40 NTU
90 mg/L Adv Coag
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.35 NTU
100 mg/L Adv Coag
Filtrate 0.08 NTU
UVT: 94.4%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.29 NTU

## Slide 36: Jars 21-24 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800 & Pre-oxidant (NaOCl)

## Slide 37: Jars 21-24: End of 5-minute flocculation (30 RPM) duration.
26 mg/L 9800
0 mg/L NaOCl
Filtrate 0.09 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.25 NTU
28 mg/L 9800
0 mg/L NaOCl
Filtrate 0.08 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.28 NTU
26 mg/L 9800
1.0 mg/L NaOCl
Filtrate 0.10 NTU
UVT: 93.1%
UVA: 0.031/cm
UVA Reduction: 18.4%
Settled: 0.32 NTU
28 mg/L 9800
1.0 mg/L NaOCl
Filtrate 0.08 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 21.1%
Settled: 0.29 NTU

## Slide 38: Jars 21-24: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 39: Jars 21-24: After 25-minutes of settling, settled water turbidity is taken.
26 mg/L 9800
0 mg/L NaOCl
Filtrate 0.09 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.25 NTU
28 mg/L 9800
0 mg/L NaOCl
Filtrate 0.08 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.28 NTU
26 mg/L 9800
1.0 mg/L NaOCl
Filtrate 0.10 NTU
UVT: 93.1%
UVA: 0.031/cm
UVA Reduction: 18.4%
Settled: 0.32 NTU
28 mg/L 9800
1.0 mg/L NaOCl
Filtrate 0.08 NTU
UVT: 93.2%
UVA: 0.030/cm
UVA Reduction: 21.1%
Settled: 0.29 NTU

## Slide 40: Jars 25-28 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890

## Slide 41: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
22 mg/L 9800
2.2 mg/L 9890
Filtrate 0.12 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.33 NTU
24 mg/L 9800
2.4 mg/L 9890
Filtrate 0.08 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.30 NTU
26 mg/L 9800
2.6 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.31 NTU
28 mg/L 9800
2.8 mg/L 9890
Filtrate 0.12 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.33 NTU

## Slide 42: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 43: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
22 mg/L 9800
2.2 mg/L 9890
Filtrate 0.12 NTU
UVT: 93.9%
UVA: 0.027/cm
UVA Reduction: 28.9%
Settled: 0.33 NTU
24 mg/L 9800
2.4 mg/L 9890
Filtrate 0.08 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.30 NTU
26 mg/L 9800
2.6 mg/L 9890
Filtrate 0.09 NTU
UVT: 94.0%
UVA: 0.026/cm
UVA Reduction: 31.6%
Settled: 0.31 NTU
28 mg/L 9800
2.8 mg/L 9890
Filtrate 0.12 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.33 NTU

## Slide 44: Jars 29-32 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 45: Jars 29-32: End of 5-minute flocculation (30 RPM) duration.
26 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.31 NTU
28 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.35 NTU
30 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.32 NTU
32 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.30 NTU

## Slide 46: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 47: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
26 mg/L 9810
Filtrate 0.10 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.31 NTU
28 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.35 NTU
30 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.3%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.32 NTU
32 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.6%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.30 NTU

## Slide 48: Jars 33-36 Test Flash Mix 30 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9810

## Slide 49: Jars 33-36: End of 5-minute flocculation (30 RPM) duration.
22 mg/L 9810
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.47 NTU
24 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.34 NTU
26 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.32 NTU
34 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 39.5%
Settled: 0.25 NTU

## Slide 50: Jars 33-36: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 51: Jars 33-36: After 25-minutes of settling, settled water turbidity is taken.
22 mg/L 9810
Filtrate 0.11 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.47 NTU
24 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.2%
UVA: 0.025/cm
UVA Reduction: 34.2%
Settled: 0.34 NTU
26 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.5%
UVA: 0.024/cm
UVA Reduction: 36.8%
Settled: 0.32 NTU
34 mg/L 9810
Filtrate 0.09 NTU
UVT: 94.7%
UVA: 0.023/cm
UVA Reduction: 39.5%
Settled: 0.25 NTU

## Slide 52: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-60 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 53: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 54: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 55: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 56: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 57: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732