## Criteria
| Is it a RB2 facility (Y/N)? | Y
| Hardness (mg/L CaCO3) | 59 |  |  |  | For Cd, Cr(III), Cu, Pb, Ni, Ag, Zn - not applicable to Se
| pH (s.u.) | 7.4
Note: DO NOT enter any value for the column that is NOT applicable
Note: Numbers in blue have formula in the cells - calculates values automatically
|  | Lowest (most stringent) Criteria e |  |  |  | Basin Plan Objectives (ug/L)- Regional Board 2 |  | Basin Plan Criteria (CTR Criteria except mercury) | [7 empty] | CTR Water Quality Criteria (ug/L)
|  |  | Human Health Criterion | Lowest Chronic Criterion | Lowest Acute Criterion | from Table 4-3 |  | Freshwater (from Table 3-4) |  |  |  | Saltwater (from Table 3-3) |  |  |  | Freshwater |  | Saltwater |  | Human Health for consumption of: |  | Factors for Metals Freshwater Criteria Calculation |  |  |  | Conversion Factor (CF) |  |  |  | Site-Specific Translators
# in CTR | PRIORITY POLLUTANTS |  |  |  |  | Shallow Water | Deep Water (24-hr) | 4-day | 1-hr | 24-hr | Inst. Max | 4-day | 1-hr | 24-hr | Inst. Max | CMC (acute) | CCC (chronic) | CMC (acute) | CCC (chronic) | Water & organisms | Organisms only | ma | ba | mc | bc | freshwater acute criteria | freshwater chronic criteria | saltwater acute criteria | saltwater chronic criteria | Acute | Chronic
|  | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L | ug/L
1 | Antimony | 4300 | 4300 | [17 empty] | 4300
2 | Arsenic | 36 |  | 36 | 69 |  |  | 150 | 340 |  |  | 36 | 69 |  |  | 340 | 150 | 69 | 36 | [6 empty] | 1 | 1 | 1 | 1
3 | Beryllium | No Criteria
4 | Cadmium | 1.6269 |  | 1.6269 | 2.4912 |  |  | 1.6269 | 2.4912 |  |  | 9.3561 | 42.2535 |  |  | 2.4912 | 1.6269 | 42.2535 | 9.3561 |  |  | 1.128 | -3.6867 | 0.7852 | -2.715 | 0.96608 | 0.93108 | 0.994 | 0.994
5a | Chromium (III) | 134.3574 |  | 134.3574 | 1127.2126 | [10 empty] | 1127.2126 | 134.3574 |  |  |  |  | 0.819 | 3.688 | 0.819 | 1.561 | 0.316 | 0.86
5b | Chromium (VI) or total Cr | 11.4345 |  | 11.4345 | 16.2933 |  |  | 11.4345 | 16.2933 |  |  | 50.3525 | 1107.7543 |  |  | 16.2933 | 11.4345 | 1107.7543 | 50.3525 | [6 empty] | 0.982 | 0.962 | 0.993 | 0.993
6 | Copper | 3.7349 |  | 3.7349 | 5.7831 |  |  | 5.9432 | 8.5152 |  |  | 3.7349 | 5.7831 |  |  | 8.5152 | 5.9432 | 5.7831 | 3.7349 |  |  | 0.9422 | -1.7 | 0.8545 | -1.702 | 0.96 | 0.96 | 0.83 | 0.83
7 | Lead | 1.6253 |  | 1.6253 | 41.7085 |  |  | 1.6253 | 41.7085 |  |  | 8.5174 | 220.8202 |  |  | 41.7085 | 1.6253 | 220.8202 | 8.5174 |  |  | 1.273 | -1.46 | 1.273 | -4.705 | 0.86788 | 0.86788 | 0.951 | 0.951
8 | Mercury | 0.025 | 0.051 | 0.025 | 2.1 |  |  | 0.025 | 2.4 |  |  | 0.025 | 2.1 | [7 empty] | 0.051
9 | Nickel | 8.2828 | 4600 | 8.2828 | 74.7475 |  |  | 33.3813 | 300.2444 |  |  | 8.2828 | 74.7475 |  |  | 300.2444 | 33.3813 | 74.7475 | 8.2828 |  | 4600 | 0.846 | 2.255 | 0.846 | 0.0584 | 0.998 | 0.997 | 0.99 | 0.99
10 | Selenium | 5 |  | 5 | 20 |  |  | 5 | 20 |  |  | 5 | 20 |  |  | 20 | 5 | 20 | 5 | [8 empty] | 0.998 | 0.88
11 | Silver | 1.0674 |  |  | 1.0674 |  |  |  | 1.0674 |  |  |  | 2.2353 |  |  | 1.6378 |  | 2.2353 |  |  |  | 1.72 | -6.52 |  |  | 0.85 |  | 0.85
12 | Thallium | 6.3 | 6.3 | [17 empty] | 6.3
13 | Zinc | 76.623 |  | 76.623 | 76.623 |  |  | 76.623 | 76.623 |  |  | 85.6237 | 95.1374 |  |  | 76.623 | 76.623 | 95.1374 | 85.6237 |  |  | 0.8473 | 0.884 | 0.8473 | 0.884 | 0.978 | 0.986 | 0.946 | 0.946
14 | Cyanide | 1 | 220000 | 1 | 1 |  |  | 5.2 | 22 |  |  | 1 | 1 |  |  | 22 | 5.2 | 1 | 1 |  | 220000
15 | Asbestos | No Criteria
16 | 2,3,7,8-TCDD (Dioxin) | 1.4e-08 | 1.4e-08 | [17 empty] | 1.4e-08
| TCDD TEQ | 1.4e-08 | 1.4e-08 | [17 empty] | 1.4e-08
17 | Acrolein | 780 | 780 | [17 empty] | 780
18 | Acrylonitrile | 0.66 | 0.66 | [17 empty] | 0.66
19 | Benzene | 71 | 71 | [17 empty] | 71
20 | Bromoform | 360 | 360 | [17 empty] | 360
21 | Carbon Tetrachloride | 4.4 | 4.4 | [17 empty] | 4.4
22 | Chlorobenzene | 21000 | 21000 | [17 empty] | 21000
23 | Chlordibromomethane | 34 | 34 | [17 empty] | 34
24 | Chloroethane | No Criteria
25 | 2-Chloroethylvinyl Ether | No Criteria
26 | Chloroform | No Criteria
27 | Dichlorobromomethane | 46 | 46 | [17 empty] | 46
28 | 1,1-Dichloroethane | No Criteria
29 | 1,2-Dichloroethane | 99 | 99 | [17 empty] | 99
30 | 1,1-Dichloroethylene | 3.2 | 3.2 | [17 empty] | 3.2
31 | 1,2-Dichloropropane | 39 | 39 | [17 empty] | 39
32 | 1,3-Dichloropropylene | 1700 | 1700 | [17 empty] | 1700
33 | Ethylbenzene | 29000 | 29000 | [17 empty] | 29000
34 | Methyl Bromide | 4000 | 4000 | [17 empty] | 4000
35 | Methyl Chloride | No Criteria
36 | Methylene Chloride | 1600 | 1600 | [17 empty] | 1600
37 | 1,1,2,2-Tetrachloroethane | 11 | 11 | [17 empty] | 11
38 | Tetrachloroethylene | 8.85 | 8.85 | [17 empty] | 8.85
39 | Toluene | 200000 | 200000 | [17 empty] | 200000
40 | 1,2-Trans-Dichloroethylene | 140000 | 140000 | [17 empty] | 140000
41 | 1,1,1-Trichloroethane | No Criteria
42 | 1,1,2-Trichloroethane | 42 | 42 | [17 empty] | 42
43 | Trichloroethylene | 81 | 81 | [17 empty] | 81
44 | Vinyl Chloride | 525 | 525 | [17 empty] | 525
45 | Chlorophenol | 400 | 400 | [17 empty] | 400
46 | 2,4-Dichlorophenol | 790 | 790 | [17 empty] | 790
47 | 2,4-Dimethylphenol | 2300 | 2300 | [17 empty] | 2300
48 | 2-Methyl-4,6-Dinitrophenol | 765 | 765 | [17 empty] | 765
49 | 2,4-Dinitrophenol | 14000 | 14000 | [17 empty] | 14000
50 | 2-Nitrophenol | No Criteria
51 | 4-Nitrophenol | No Criteria
52 | 3-Methyl-4-Chlorophenol | No Criteria
53 | Pentachlorophenol | 7.9 | 8.2 | 7.9 | 13 | [10 empty] | 13.0397 | 10.0041 | 13 | 7.9 |  | 8.2
54 | Phenol | 4600000 | 4600000 | [17 empty] | 4600000
55 | 2,4,6-Trichlorophenol | 6.5 | 6.5 | [17 empty] | 6.5
56 | Acenaphthene | 2700 | 2700 | [17 empty] | 2700
57 | Acenephthylene | No Criteria
58 | Anthracene | 110000 | 110000 | [17 empty] | 110000
59 | Benzidine | 0.00054 | 0.00054 | [17 empty] | 0.00054
60 | Benzo(a)Anthracene | 0.049 | 0.049 | [17 empty] | 0.049
61 | Benzo(a)Pyrene | 0.049 | 0.049 | [17 empty] | 0.049
62 | Benzo(b)Fluoranthene | 0.049 | 0.049 | [17 empty] | 0.049
63 | Benzo(ghi)Perylene | No Criteria
64 | Benzo(k)Fluoranthene | 0.049 | 0.049 | [17 empty] | 0.049
65 | Bis(2-Chloroethoxy)Methane | No Criteria
66 | Bis(2-Chloroethyl)Ether | 1.4 | 1.4 | [17 empty] | 1.4
67 | Bis(2-Chloroisopropyl)Ether | 170000 | 170000 | [17 empty] | 170000
68 | Bis(2-Ethylhexyl)Phthalate | 5.9 | 5.9 | [17 empty] | 5.9
69 | 4-Bromophenyl Phenyl Ether | No Criteria
70 | Butylbenzyl Phthalate | 5200 | 5200 | [17 empty] | 5200
71 | 2-Chloronaphthalene | 4300 | 4300 | [17 empty] | 4300
72 | 4-Chlorophenyl Phenyl Ether | No Criteria
73 | Chrysene | 0.049 | 0.049 | [17 empty] | 0.049
74 | Dibenzo(a,h)Anthracene | 0.049 | 0.049 | [17 empty] | 0.049
75 | 1,2-Dichlorobenzene | 17000 | 17000 | [17 empty] | 17000
76 | 1,3-Dichlorobenzene | 2600 | 2600 | [17 empty] | 2600
77 | 1,4-Dichlorobenzene | 2600 | 2600 | [17 empty] | 2600
78 | 3,3'-Dichlorobenzidine | 0.077 | 0.077 | [17 empty] | 0.077
79 | Diethyl Phthalate | 120000 | 120000 | [17 empty] | 120000
80 | Dimethyl Phthalate | 2900000 | 2900000 | [17 empty] | 2900000
81 | Di-n-Butyl Phthalate | 12000 | 12000 | [17 empty] | 12000
82 | 2,4-Dinitrotoluene | 9.1 | 9.1 | [17 empty] | 9.1
83 | 2,6-Dinitrotoluene | No Criteria
84 | Di-n-Octyl Phthalate | No Criteria
85 | 1,2-Diphenylhydrazine | 0.54 | 0.54 | [17 empty] | 0.54
86 | Fluoranthene | 370 | 370 | [17 empty] | 370
87 | Fluorene | 14000 | 14000 | [17 empty] | 14000
88 | Hexachlorobenzene | 0.00077 | 0.00077 | [17 empty] | 0.00077
89 | Hexachlorobutadiene | 50 | 50 | [17 empty] | 50
90 | Hexachlorocyclopentadiene | 17000 | 17000 | [17 empty] | 17000
91 | Hexachloroethane | 8.9 | 8.9 | [17 empty] | 8.9
92 | Indeno(1,2,3-cd) Pyrene | 0.049 | 0.049 | [17 empty] | 0.049
93 | Isophorone | 600 | 600 | [17 empty] | 600
94 | naphthalene | No Criteria
95 | Nitrobenzene | 1900 | 1900 | [17 empty] | 1900
96 | N-Nitrosodimethylamine | 8.1 | 8.1 | [17 empty] | 8.1
97 | N-Nitrosodi-n-Propylamine | 1.4 | 1.4 | [17 empty] | 1.4
98 | N-Nitrosodiphenylamine | 16 | 16 | [17 empty] | 16
99 | Phenanthrene | No Criteria
100 | Pyrene | 11000 | 11000 | [17 empty] | 11000
101 | 1,2,4-Trichlorobenzene | No Criteria
102 | Aldrin | 0.00014 | 0.00014 |  | 1.3 | [10 empty] | 3 |  | 1.3 |  |  | 0.00014
103 | alpha-BHC | 0.013 | 0.013 | [17 empty] | 0.013
104 | beta-BHC | 0.046 | 0.046 | [17 empty] | 0.046
105 | gamma-BHC | 0.063 | 0.063 |  | 0.16 | [10 empty] | 0.95 |  | 0.16 |  |  | 0.063
106 | delta-BHC | No Criteria
107 | Chlordane | 0.00059 | 0.00059 | 0.004 | 0.09 | [10 empty] | 2.4 | 0.0043 | 0.09 | 0.004 |  | 0.00059
108 | 4,4-DDT | 0.00059 | 0.00059 | 0.001 | 0.13 | [10 empty] | 1.1 | 0.001 | 0.13 | 0.001 |  | 0.00059
109 | 4,4-DDE | 0.00059 | 0.00059 | [17 empty] | 0.00059
110 | 4,4-DDD | 0.00084 | 0.00084 | [17 empty] | 0.00084
111 | Dieldrin | 0.00014 | 0.00014 | 0.0019 | 0.24 | [10 empty] | 0.24 | 0.056 | 0.71 | 0.0019 |  | 0.00014
112 | alpha-Endosulfan | 0.0087 | 240 | 0.0087 | 0.034 | [10 empty] | 0.22 | 0.056 | 0.034 | 0.0087 |  | 240
113 | beta-Endosulfan | 0.0087 | 240 | 0.0087 | 0.034 | [10 empty] | 0.22 | 0.056 | 0.034 | 0.0087 |  | 240
114 | Endosulfan Sulfate | 240 | 240 | [17 empty] | 240
115 | Endrin | 0.0023 | 0.81 | 0.0023 | 0.037 | [10 empty] | 0.086 | 0.036 | 0.037 | 0.0023 |  | 0.81
116 | Endrin Aldehyde | 0.81 | 0.81 | [17 empty] | 0.81
117 | Heptachlor | 0.00021 | 0.00021 | 0.0036 | 0.053 | [10 empty] | 0.52 | 0.0038 | 0.053 | 0.0036 |  | 0.00021
118 | Heptchlor Epoxide | 0.00011 | 0.00011 | 0.0036 | 0.053 | [10 empty] | 0.52 | 0.0038 | 0.053 | 0.0036 |  | 0.00011
119-125 | PCBs sum (2) | 0.00017 | 0.00017 | 0.014 | [12 empty] | 0.014 |  | 0.03 |  | 0.00017
126 | Toxaphene | 0.0002 | 0.00075 | 0.0002 | 0.21 | [10 empty] | 0.73 | 0.0002 | 0.21 | 0.0002 |  | 0.00075
| Tributyltin | 0.01 |  | 0.01 | [7 empty] | 0.01
| Total PAHs | 15 |  | 15 | [9 empty] | 15
Notes:
(2) | PCBs sum refers to sum of PCB 1016, 1221, 1232, 1242, 1248, 1254, and 1260
Note on B1: RB2: BP criteria selected for As, Cd, Cr, Pb, Hg, Ni, Se, Ag, Zn, and CN - for waters in the region except for South Bay below Dumbarton Bridge.
Note on W8: Table 1 of paragraph b(2) - page 31717 of CTR
Note on AA8: Table 2 of paragraph b(2) - page 31717 of CTR
Note on B12: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on B14: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on I14: see footnote 'e' in BP, Table 3-4
Note on J14: see footnote 'e' in BP, Table 3-4
Note on Q14: used eq in paragraph b(2) - page 31717 of CTR
Note on R14: used eq in paragraph b(2) - page 31717 of CTR
Note on S14: These reflect the values in the CTR, not the revised Cd criteria published in April 2000.
Note on W14: These reflect the values in the CTR, not the revised Cd criteria/factors published in April 2000.
Note on AA14: used eq in Table 3 of paragraph (b)(2)- page 31717 of CTR
Note on AB14: used eq in Table 3 of paragraph (b)(2)- page 31717 of CTR
Note on Q15: used eq in paragraph b(2) - page 31717 of CTR
Note on R15: used eq in paragraph b(2) - page 31717 of CTR
Note on B16: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on I17: see footnote 'g' in BP, Table 3-4
Note on J17: see footnote 'g' in BP, Table 3-4
Note on Q17: used eq in paragraph b(2) - page 31717 of CTR
Note on R17: used eq in paragraph b(2) - page 31717 of CTR
Note on B18: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on I18: see footnote 'h' in BP, Table 3-4
Note on J18: see footnote 'h' in BP, Table 3-4
Note on Q18: used eq in paragraph b(2) - page 31717 of CTR
Note on R18: used eq in paragraph b(2) - page 31717 of CTR
Note on AA18: used eq in Table 3 of paragraph (b)(2)- page 31717 of CTR
Note on AB18: used eq in Table 3 of paragraph (b)(2)- page 31717 of CTR
Note on B19: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on I19: although 0.012 is desirable, compliance can only be met at 0.025 det. Limit. See BP footnote for details. Table 3-4.
Note on B20: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on Q20: used eq in paragraph b(2) - page 31717 of CTR
Note on R20: used eq in paragraph b(2) - page 31717 of CTR
Note on Q21: see footnote 'p'
Note on S21: Refer to CTR, footnotes p and q, for explanation. NTR values apply to Suisun Bay, both freshwater and saltwater values.
Note on T21: Refer to CTR, footnotes p and q, for explanation. NTR values apply to Suisun Bay, both freshwater and saltwater values.
Note on B22: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on L22: see footnote 'k' in BP, Table 3-4
Note on Q22: used eq in paragraph b(2) - page 31717 of CTR
Note on B24: select BP criteria for RB2 except for So. Bay below Dumbarton Bridge
Note on I24: see footnote 'j'in BP, Table 3-4 5/1/02 Formula corrected per BP Amendments 2/1997.
Note on J24: see footnote 'g'in BP, Table 3-4 5/1/02 Formula corrected per BP Amendments 2/1997.
Note on Q24: used eq in paragraph b(2) - page 31717 of CTR
Note on R24: used eq in paragraph b(2) - page 31717 of CTR
Note on Q65: see footnote 'f'
Note on R65: see footnote 'f'
Note on M133: It is an EPA revised criteria (sw). For details, see email from RB2 (LR).
Note on AC17: Ken Katen: From revised translator data, LWA, 7-19-04.
Note on AD17: Ken Katen: From revised translator data, LWA, 7-19-04.
Note on AC20: Ken Katen: From revised translator data, LWA, 7-19-04.
Note on AD20: Ken Katen: From revised translator data, LWA, 7-19-04.

## data input for RPA
Green highlight checks for input inconsistency (see "input check" spreadsheet for logic)
Yellow highlights are user input
|  | EFFLUENT DATA |  |  |  |  | BACKGROUND DATA (B)
CTR No. | Constituent name | Effluent Data Available (Y/N)? | Are all data points non-detects (Y/N)? | If all data points ND Enter the min detection limit (MDL) (ug/L) | Enter the pollutant effluent detected max conc (ug/L) |  | B Available (Y/N)? | Are all B non-detects (Y/N)? | If all data points ND Enter the min detection limit (MDL) (ug/L) |  |  | 7) Review other information in the SIP page 4. If information is unavailable or insufficient: 8) the RWQCB shall establish interim monitoring requirements.
[6 empty] | Input Check |  |  |  | Enter the Detected Maximum Background Conc | Input Check
1 | Antimony | Y | N |  | 1.02 |  | Y | N |  | 1.8
2 | Arsenic | Y | N |  | 28.2 |  | Y | N |  | 2.46 |  |  | Total
3 | Beryllium | Y | Y | 0.2 |  |  | Y | N |  | 0.215 |  | No Criteria
4 | Cadmium | Y | N |  | 0.2 |  | Y | N |  | 0.1268 |  |  | Total
5a | Chromium (III) | Y | N |  | 2.86 |  | N | [5 empty] | Total
5b | Chromium (VI) | Y | N |  | 1.44 |  | Y | N |  | 4.4 |  |  | Can be met as total Cr.
6 | Copper | Y | N |  | 6.73 |  | Y | N |  | 2.45 |  |  | Total
7 | Lead | Y | N |  | 2.68 |  | Y | N |  | 0.8 |  |  | Total
8 | Mercury | Y | N |  | 0.11 |  | Y | N |  | 0.0086 |  |  | Total
9 | Nickel | Y | N |  | 37.8 |  | Y | N |  | 3.7 |  |  | Total
10 | Selenium | Y | N |  | 22.1 |  | Y | N |  | 0.39 |  |  | Total
11 | Silver | Y | Y | 0.5 |  |  | Y | N |  | 0.0516 |  |  | Total
12 | Thallium | Y | N |  | 1.46 |  | Y | N |  | 0.21 |  |  | Total
13 | Zinc | Y | N |  | 50.41 |  | Y | N |  | 4.4 |  |  | Total
14 | Cyanide | Y | N |  | 4.8 |  | Y | Y | 0.4 |  |  |  | Total
15 | Asbestos | [5 empty] | N |  |  |  |  | No Criteria
16 | 2,3,7,8 TCDD-TEQ | Y | Y |  |  |  | Y | N |  | 7.1e-08
17 | Acrolein | Y | Y | 0.5 |  |  | Y | Y | 0.5
18 | Acrylonitrile | Y | Y | 2 |  |  | Y | N |  | 0.03
19 | Benzene | Y | Y | 0.5 |  |  | Y | Y | 0.05
20 | Bromoform | Y | Y | 0.5 |  |  | Y | Y | 0.5
21 | Carbon Tetrachloride | Y | Y | 0.5 |  |  | Y | N |  | 0.06
22 | Chlorobenzene | Y | Y | 0.5 |  |  | Y | Y | 0.5
23 | Chlorodibromomethane | Y | Y | 0.5 |  |  | Y | Y | 0.05
24 | Chloroethane | Y | y | 0.5 |  |  | Y | Y | 0.5 |  |  | No Criteria
25 | 2-Chloroethylvinyl ether | Y | Y | 0.5 |  |  | Y | Y | 0.5 |  |  | No Criteria
26 | Chloroform | Y | N |  | 0.9 |  | Y | Y | 0.5 |  |  | No Criteria
27 | Dichlorobromomethane | Y | Y | 0.5 |  |  | Y | Y | 0.05
28 | 1,1-Dichloroethane | Y | Y | 0.5 |  |  | Y | Y | 0.05 |  |  | No Criteria
29 | 1,2-Dichloroethane | Y | Y | 0.5 |  |  | Y | N |  | 0.04
30 | 1,1-Dichloroethylene | Y | Y | 0.5 |  |  | Y | Y | 0.5
31 | 1,2-Dichloropropane | Y | Y | 0.5 |  |  | Y | Y | 0.05
32 | 1,3-Dichloropropylene | Y | Y | 0.5 |  |  | N
33 | Ethylbenzene | Y | Y | 0.5 |  |  | Y | Y | 0.5
34 | Methyl Bromide | Y | Y | 0.5 |  |  | Y | Y | 0.5
35 | Methyl Chloride | Y | Y | 0.5 |  |  | Y | Y | 0.5 |  |  | No Criteria
36 | Methylene Chloride | Y | N |  | 2 |  | Y | N |  | 0.5
37 | 1,1,2,2-Tetrachloroethane | Y | Y | 0.5 |  |  | Y | Y | 0.05
38 | Tetrachloroethylene | Y | N |  | 0.5 |  | Y | Y | 0.05
39 | Toluene | Y | Y | 0.5 |  |  | Y | Y | 0.3
40 | 1,2-Trans-Dichloroethylene | Y | Y | 0.5 |  |  | Y | Y | 0.5
41 | 1,1,1-Trichloroethane | Y | Y | 0.5 |  |  | Y | Y | 0.5 |  |  | No Criteria
42 | 1,1,2-Trichloroethane | Y | Y | 0.5 |  |  | Y | Y | 0.05
43 | Trichloroethylene | Y | Y | 0.5 |  |  | Y | Y | 0.5
44 | Vinyl Chloride | Y | Y | 0.5 |  |  | Y | Y | 0.5
45 | 2-Chlorophenol | Y | Y | 2 |  |  | Y | Y | 1.2
46 | 2,4-Dichlorophenol | Y | Y | 1 |  |  | Y | Y | 1.3
47 | 2,4-Dimethylphenol | Y | Y | 2 |  |  | Y | Y | 1.3
48 | 2-Methyl- 4,6-Dinitrophenol | Y | Y | 5 |  |  | Y | Y | 1.2
49 | 2,4-Dinitrophenol | Y | Y | 5 |  |  | Y | Y | 0.7
50 | 2-Nitrophenol | Y | Y | 5 |  |  | Y | Y | 1.3 |  |  | No Criteria
51 | 4-Nitrophenol | Y | Y | 5 |  |  | Y | Y | 1.6 |  |  | No Criteria
52 | 3-Methyl 4-Chlorophenol | Y | Y | 1 |  |  | Y | Y | 1.1 |  |  | No Criteria
53 | Pentachlorophenol | Y | Y | 1 |  |  | Y | Y | 1
54 | Phenol | Y | Y | 1 |  |  | Y | Y | 1.3
55 | 2,4,6-Trichlorophenol | Y | N |  | 5 |  | Y | Y | 1.3
56 | Acenaphthene | Y | Y | 0.3 |  |  | Y | N |  | 0.0015
57 | Acenaphthylene | Y | Y | 0.2 |  |  | Y | N |  | 0.00053 |  | No Criteria
58 | Anthracene | Y | Y | 0.3 |  |  | Y | N |  | 0.0005
59 | Benzidine | Y | Y | 5 |  |  | Y | Y | 0.0015
60 | Benzo(a)Anthracene | Y | Y | 0.1 |  |  | Y | N |  | 0.0053
61 | Benzo(a)Pyrene | Y | Y | 0.3 |  |  | Y | N |  | 0.00029
62 | Benzo(b)Fluoranthene | Y | Y | 0.3 |  |  | Y | N |  | 0.0046
63 | Benzo(ghi)Perylene | Y | Y | 0.3 |  |  | Y | N |  | 0.0027 |  | No Criteria
64 | Benzo(k)Fluoranthene | Y | Y | 0.3 |  |  | Y | N |  | 0.0015
65 | Bis(2-Chloroethoxy)Methane | Y | Y | 2 |  |  | Y | Y | 0.3 |  |  | No Criteria
66 | Bis(2-Chloroethyl)Ether | Y | Y | 1 |  |  | Y | Y | 0.3
67 | Bis(2-Chloroisopropyl)Ether | Y | Y | 2 |  |  | N
68 | Bis(2-Ethylhexyl)Phthalate | Y | Y | 1 |  |  | Y | Y | 0.5
69 | 4-Bromophenyl Phenyl Ether | Y | Y | 5 |  |  | Y | Y | 0.23 |  |  | No Criteria
70 | Butylbenzyl Phthalate | Y | Y | 2 |  |  | Y | Y | 0.52
71 | 2-Chloronaphthalene | Y | Y | 2 |  |  | Y | Y | 0.3
72 | 4-Chlorophenyl Phenyl Ether | Y | Y | 5 |  |  | Y | Y | 0.3 |  |  | No Criteria
73 | Chrysene | Y | Y | 0.3 |  |  | Y | N |  | 0.0024
74 | Dibenzo(a,h)Anthracene | Y | Y | 0.1 |  |  | Y | N |  | 0.00064
75 | 1,2-Dichlorobenzene | N |  |  |  |  | Y | Y | 0.8
76 | 1,3-Dichlorobenzene | Y | Y | 0.5 |  |  | Y | Y | 0.8
77 | 1,4-Dichlorobenzene | Y | Y | 0.5 |  |  | Y | Y | 0.8
78 | 3,3 Dichlorobenzidine | Y | Y | 5 |  |  | Y | Y | 0.001
79 | Diethyl Phthalate | Y | Y | 2 |  |  | Y | Y | 0.24
80 | Dimethyl Phthalate | Y | Y | 2 |  |  | Y | Y | 0.24
81 | Di-n-Butyl Phthalate | Y | Y | 5 |  |  | Y | Y | 0.5
82 | 2,4-Dinitrotoluene | Y | Y | 5 |  |  | Y | Y | 0.27
83 | 2,6-Dinitrotoluene | Y | Y | 5 |  |  | Y | Y | 0.29 |  |  | No Criteria
84 | Di-n-Octyl Phthalate | Y | Y | 5 |  |  | Y | Y | 0.38 |  |  | No Criteria
85 | 1,2-Diphenylhydrazine | Y | Y | 1 |  |  | Y | N |  | 0.0037
86 | Fluoranthene | Y | Y | 0.05 |  |  | Y | N |  | 0.011
87 | Fluorene | Y | Y | 0.1 |  |  | Y | N |  | 0.00208
88 | Hexachlorobenzene | Y | Y | 0.1 |  |  | Y | N |  | 2.02e-05
89 | Hexachlorobutadiene | Y | Y | 1 |  |  | Y | Y | 0.3
90 | Hexachlorocyclopentadiene | Y | Y | 5 |  |  | Y | Y | 0.31
91 | Hexachloroethane | Y | Y | 1 |  |  | Y | Y | 0.2
92 | Indeno(1,2,3-cd)Pyrene | Y | Y | 0.05 |  |  | Y | N |  | 0.004
93 | Isophorone | Y | Y | 1 |  |  | Y | Y | 0.3
94 | Naphthalene | Y | Y | 0.2 |  |  | Y | N |  | 0.0023 |  | No Criteria
95 | Nitrobenzene | Y | Y | 1 |  |  | Y | Y | 0.25
96 | N-Nitrosodimethylamine | Y | Y | 1 |  |  | Y | Y | 0.3
97 | N-Nitrosodi-n-Propylamine | Y | Y | 5 |  |  | Y | Y | 0.001
98 | N-Nitrosodiphenylamine | Y | Y | 1 |  |  | Y | Y | 0.001
99 | Phenanthrene | Y | Y | 0.05 |  |  | Y | N |  | 0.0061 |  | No Criteria
100 | Pyrene | Y | Y | 0.05 |  |  | Y | N |  | 0.0051
101 | 1,2,4-Trichlorobenzene | Y | Y | 5 |  |  | Y | Y | 0.3 |  |  | No Criteria
102 | Aldrin | Y | Y | 0.005 |  |  | N
103 | alpha-BHC | Y | Y | 0.01 |  |  | Y | N |  | 0.000496
104 | beta-BHC | Y | Y | 0.005 |  |  | Y | N |  | 0.000413
105 | gamma-BHC | Y | Y | 0.01 |  |  | Y | N |  | 0.0007034
106 | delta-BHC | Y | Y | 0.01 |  |  | Y | N |  | 4.2e-05 |  | No Criteria
107 | Chlordane | Y | Y | 0.02 |  |  | Y | N |  | 0.00018
108 | 4,4'-DDT | Y | Y | 0.01 |  |  | Y | N |  | 6.6e-05
109 | 4,4'-DDE (linked to DDT) | Y | Y | 0.01 |  |  | Y | N |  | 0.000693
110 | 4,4'-DDD | Y | Y | 0.01 |  |  | Y | N |  | 0.000313
111 | Dieldrin | Y | Y | 0.01 |  |  | Y | N |  | 0.000264
112 | alpha-Endosulfan | Y | Y | 0.01 |  |  | Y | N |  | 3.1e-05
113 | beta-Endolsulfan | Y | Y | 0.01 |  |  | Y | N |  | 6.9e-05
114 | Endosulfan Sulfate | Y | Y | 0.01 |  |  | Y | N |  | 8.19e-05
115 | Endrin | Y | Y | 0.01 |  |  | Y | N |  | 3.6e-05
116 | Endrin Aldehyde | Y | Y | 0.01 |  |  | N
117 | Heptachlor | Y | Y | 0.01 |  |  | Y | N |  | 1.9e-05
118 | Heptachlor Epoxide | Y | N |  | 0.1 |  | Y | N |  | 2.458e-05
119-125 | PCBs sum | Y | N |  | 0.000651 |  | N
126 | Toxaphene | Y | Y | 0.05 |  |  | N
| Tributylin |  |  |  |  | Check input | Y | Y | 0.001
| Total PAHs | Y | Y | 0.1 |  |  | Y | N |  | 0.26
| Chlorpyrifos |  | y | 0.05
| Diazinon |  | y | 0.05
note background for heptachlor epoxide is average so limit calculation is correct
Note on D6: Enter data if it is an "Y" in the 1st column to the left
Note on E6: Enter data only if there is an 'Y' in 1st column to the left
Note on F6: Enter data only if there is 'N' in 2nd column to the left and 'Y' in 3rd column to the left
Note on J6: Enter data if it is an "Y" in the 1st column to the left
Note on K6: Enter data only if there is an 'Y' in 1st column to the left
Note on F28: Ken Katen: Based on 4/1/03, Ignacio ND, Novato 3.91.
Note on F31: Ken Katen: Based on 4/1/03, Ignacio ND, Novato 7.3.
Note on L7: Ken Katen: Taken from 1993-2001 RMP data as downloaded from SFEI. See worksheet in folder.

## CV Calculator
Date | Copper | Nickel | Cyanide | Date | Mercury | Date | Selenium
2003-01-07 | 2.95 | 20.2 | 1.5 | 2003-01-07 | 0.0123 | 2003-01-07 | 5.16
2003-02-05 | 2.2 | 22.3 | 1.5 | 2003-01-13 | 0.016 | 2003-01-15 | 4.52
2003-03-05 | 1.39 | 16.9 | 1.5 | 2003-01-14 | 0.015 | 2003-01-23 | 11.1
2003-04-02 | 1.81 | 14.4 | 1.5 | 2003-01-15 | 0.011 | 2003-01-28 | 6.6
2003-05-06 | 2.05 | 18.7 | 1.5 | 2003-01-16 | 0.011 | 2003-02-05 | 3.64
2003-06-03 | 3.54 | 26.3 | 1.5 | 2003-01-22 | 0.011 | 2003-02-13 | 14.4
2003-07-08 | 2.57 | 23.2 | 1.5 | 2003-01-29 | 0.012 | 2003-02-18 | 13.2
2003-08-05 | 2.89 | 19.7 | 1.5 | 2003-02-04 | 0.01 | 2003-02-26 | 9.47
2003-09-03 | 1.83 | 15 | 1.5 | 2003-02-12 | 0.0088 | 2003-03-06 | 9.62
2003-10-02 | 6.5 | 14.9 | 1.5 | 2003-02-20 | 0.0081 | 2003-03-11 | 10.9
2003-11-04 | 0.5 | 19.8 | 1.5 | 2003-02-26 | 0.11 | 2003-03-19 | 6.14
2003-12-04 | 2.05 | 18.3 | 1.5 | 2003-03-05 | 0.0067 | 2003-03-27 | 3.46
2004-01-06 | 3.95 | 27.4 | 1.5 | 2003-04-02 | 0.0012 | 2003-04-02 | 5.08
2004-02-04 | 3.06 | 22.9 | 1.5 | 2003-05-06 | 0.001 | 2003-04-10 | 12.7
2004-03-04 | 3.98 | 23.7 | 1.5 | 2003-06-02 | 0.0098 | 2003-04-15 | 11.2
2004-04-07 | 1.83 | 13.4 | 1.5 | 2003-07-07 | 0.008 | 2003-04-23 | 9.78
2004-05-06 | 2.81 | 15.4 | 1.5 | 2003-08-04 | 0.0064 | 2003-05-01 | 10.8
2004-06-02 | 1.05 | 15.1 | 1.5 | 2003-09-03 | 0.0098 | 2003-05-06 | 10.4
2004-07-08 | 2.87 | 17.4 | 1.5 | 2003-10-01 | 0.005 | 2003-05-13 | 13.98
2004-08-05 | 0.73 | 11.5 | 1.5 | 2003-11-03 | 0.0082 | 2003-05-21 | 14.4
2004-09-08 | 2.08 | 15.2 | 1.5 | 2003-12-03 | 0.018 | 2003-05-27 | 17.1
2004-10-07 | 0.64 | 19.9 | 1.5 | 2004-01-06 | 0.015 | 2003-06-02 | 15.9
2004-11-02 | 3.09 | 18.7 | 1.5 | 2004-02-03 | 0.0086 | 2003-06-10 | 12.7
2004-12-06 | 1.22 | 15.1 | 1.5 | 2004-03-03 | 0.013 | 2003-06-19 | 15.1
2005-01-06 | 0.76 | 37.8 | 1.5 | 2004-04-06 | 0.006 | 2003-06-24 | 14
2005-02-03 | 6.73 | 17 | 4.8 | 2004-05-05 | 0.0089 | 2003-07-03 | 16.6
2005-03-03 | 4.88 | 19.5 | 1.5 | 2004-06-01 | 0.0087 | 2003-07-08 | 19.8
2005-04-08 | 2.17 | 15.6 | 1.5 | 2004-07-06 | 0.015 | 2003-07-15 | 13.9
2005-05-06 | 2.96 | 16.9 | 4.2 | 2004-08-05 | 0.0086 | 2003-07-23 | 15
2005-06-03 | 2.25 | 15 | 1.7 | 2004-09-08 | 0.0078 | 2003-07-30 | 18.9
2005-07-06 | 2.45 | 16.9 | 1.9 | 2004-10-07 | 0.0065 | 2003-08-05 | 17.1
2005-08-02 | 2.22 | 14.2 | 3.5 | 2004-11-02 | 0.012 | 2003-08-13 | 14.2
2005-09-08 | 1.68 | 16 | 3.3 | 2004-12-06 | 0.012 | 2003-08-21 | 12.7
2005-10-06 | 3.17 | 13 | 1.7 | 2005-01-06 | 0.02 | 2003-08-26 | 11.8
2005-11-03 | 3.33 | 14 | 1.4 | 2005-02-02 | 0.014 | 2003-09-03 | 20.7
2005-12-06 | 4.7 | 28 | 1.8 | 2005-03-03 | 0.026 | 2003-09-11 | 22.1
|  |  |  | 2005-04-08 | 0.019 | 2003-09-16 | 21.8
Average | 2.6358 | 18.5917 | 1.8 | 2005-05-06 | 0.015 | 2003-09-24 | 6.27
Stand Dev | 1.4469 | 5.2432 | 0.80214 | 2005-06-02 | 0.007 | 2003-10-02 | 6.25
Coeff Var | 0.54894 | 0.28202 | 0.44563 | 2005-06-03 | 0.007 | 2003-10-07 | 5.63
CV (round) | 0.549 | 0.282 | 0.446 | 2005-07-06 | 0.0063 | 2003-10-15 | 8.97
|  |  |  | 2005-08-02 | 0.0082 | 2003-10-23 | 6.12
|  |  |  | 2005-09-08 | 0.0098 | 2003-10-28 | 4.84
|  |  |  | 2005-10-06 | 0.013 | 2003-11-05 | 6.98
|  |  |  | 2005-11-03 | 0.0059 | 2003-11-13 | 6.12
|  |  |  | 2005-12-06 | 0.0275 | 2003-11-18 | 6.6
[6 empty] | 2003-11-26 | 6.12
|  |  |  | Average | 0.013046 | 2003-12-04 | 15.6
|  |  |  | Stand Dev | 0.015551 | 2003-12-09 | 14.5
|  |  |  | Coeff Var | 1.192 | 2003-12-17 | 14
|  |  |  | CV (round) | 1.192 | 2003-12-23 | 9.64
[6 empty] | 2003-12-31 | 11.1
[6 empty] | 2004-01-06 | 7.99
[6 empty] | 2004-01-14 | 6.79
[6 empty] | 2004-01-22 | 7.94
[6 empty] | 2004-01-27 | 6.13
[6 empty] | 2004-02-04 | 5.85
[6 empty] | 2004-02-12 | 4.84
[6 empty] | 2004-02-17 | 6.62
[6 empty] | 2004-02-25 | 5.95
[6 empty] | 2004-03-04 | 5.57
[6 empty] | 2004-03-09 | 6.04
[6 empty] | 2004-03-17 | 5.57
[6 empty] | 2004-03-25 | 7.39
[6 empty] | 2004-03-30 | 6.33
[6 empty] | 2004-04-07 | 7.89
[6 empty] | 2004-04-15 | 7.21
[6 empty] | 2004-04-20 | 8.13
[6 empty] | 2004-04-28 | 11.1
[6 empty] | 2004-05-06 | 13.7
[6 empty] | 2004-05-11 | 15.5
[6 empty] | 2004-05-19 | 15.3
[6 empty] | 2004-05-27 | 16.7
[6 empty] | 2004-06-02 | 15.4
[6 empty] | 2004-06-10 | 9.04
[6 empty] | 2004-06-15 | 7.28
[6 empty] | 2004-06-23 | 10.5
[6 empty] | 2004-06-30 | 5.78
[6 empty] | 2004-07-07 | 8.02
[6 empty] | 2004-07-15 | 8.95
[6 empty] | 2004-07-20 | 9.44
[6 empty] | 2004-07-28 | 12.4
[6 empty] | 2004-08-05 | 16.2
[6 empty] | 2004-08-10 | 13.1
[6 empty] | 2004-08-18 | 12.6
[6 empty] | 2004-08-26 | 12
[6 empty] | 2004-08-31 | 8.04
[6 empty] | 2004-09-08 | 4.82
[6 empty] | 2004-09-16 | 9.14
[6 empty] | 2004-09-22 | 6.28
[6 empty] | 2004-09-29 | 7.4
[6 empty] | 2004-10-07 | 7.2
[6 empty] | 2004-10-12 | 8.6
[6 empty] | 2004-10-20 | 13
[6 empty] | 2004-10-28 | 12.9
[6 empty] | 2004-11-02 | 9.86
[6 empty] | 2004-11-10 | 8.66
[6 empty] | 2004-11-18 | 8.46
[6 empty] | 2004-11-24 | 8.3
[6 empty] | 2004-11-30 | 10.2
[6 empty] | 2004-12-07 | 8.67
[6 empty] | 2004-12-15 | 10.7
[6 empty] | 2004-12-22 | 8.76
[6 empty] | 2004-12-29 | 21.1
[6 empty] | 2005-01-06 | 9.4
[6 empty] | 2005-01-14 | 8.48
[6 empty] | 2005-01-19 | 8.1
[6 empty] | 2005-01-26 | 8.13
[6 empty] | 2005-02-03 | 6.71
[6 empty] | 2005-02-11 | 7.54
[6 empty] | 2005-02-15 | 8.07
[6 empty] | 2005-02-23 | 7.14
[6 empty] | 2005-03-03 | 7.16
[6 empty] | 2005-03-11 | 5.69
[6 empty] | 2005-03-15 | 5.85
[6 empty] | 2005-03-23 | 13.87
[6 empty] | 2005-03-31 | 9.06
[6 empty] | 2005-04-08 | 18.04
[6 empty] | 2005-04-12 | 14.1
[6 empty] | 2005-04-20 | 14.7
[6 empty] | 2005-04-28 | 14.2
[6 empty] | 2005-05-06 | 14.13
[6 empty] | 2005-05-10 | 9.61
[6 empty] | 2005-05-18 | 6.89
[6 empty] | 2005-05-26 | 4.89
[6 empty] | 2005-06-03 | 11.2
[6 empty] | 2005-07-05 | 11.5
[6 empty] | 2005-07-14 | 8.48
[6 empty] | 2005-07-22 | 11.3
[6 empty] | 2005-07-27 | 13.1
[6 empty] | 2005-08-02 | 18.7
[6 empty] | 2005-09-08 | 16.6
[6 empty] | 2005-10-06 | 19.55
[6 empty] | 2005-11-03 | 14.6
[6 empty] | 2005-12-07 | 8.85
[6 empty] | 2005-12-16 | 5.98
[6 empty] | 2005-12-20 | 14.81
[6 empty] | 2005-12-29 | 21.04
[6 empty] | Average | 10.6051
[6 empty] | Stand Dev | 4.3835
[6 empty] | Coeff Var | 0.41334
[6 empty] | CV (round) | 0.413

## RPA
Beginning |  |  | Step 2 | Step 3 |  |  |  |  | Step 4 |  | Step 2 | Step 3 |  | Step 4. | Step 5. | Step 6. | Step 7 & 8. | Combined Effluent Final Result, Flow Weighted Averages
| Constituent name | C (mg/L) | Effluent Data Available? | Are all data points non-detects? | Minimum MDL (ug/L) if all data ND. | Enter the pollutant effluent detected max conc (ug/L) | If all data points are ND and MinDL>C, interim monitoring is required | Maximum Pollutant Concentration (MEC) (ug/L) | MEC vs. C |  | Background Data Available? | Are all B data points non-detects? | If all data points ND Enter the min detection limit (MDL) (ug/L) | Enter the pollutant B detected max conc (ug/L) | If all B is ND, is MDL>C? (If Y, Go To Step 7) | B vs. C | 7) Review other information in the SIP page 4. Y if other information indicates limits are required. If information is unavailable or insufficient: 8) the RWQCB shall establish interim monitoring requirements.
|  | Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) | [5 empty] | (MEC= deteted max value; if all ND & MDL<C then MEC = MDL) | Y if If MEC >= C, effluent limitation is required; 2. If MEC<C, go to Step 5 | [6 empty] | If B>C, effluent limitation is required |  | RPA Result | Reason | Daily Max, ug/l | Monthly Average, ug/l
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | r | S | T
1 | Antimony | 4300 | Y | N |  | 1.02 |  | 1.02 | MEC<C, go to Step 5 |  | Y |  |  | 1.8 |  | B<C, Step 7
2 | Arsenic b | 36 | Y | N |  | 28.2 |  | 28.2 | MEC<C, go to Step 5 |  | Y |  |  | 2.46 |  | B<C, Step 7
3 | Beryllium | No Criteria | Y | Y | 0.2 |  | No Criteria | 0.2 | No Criteria |  | Y |  |  | 0.215 |  | No Criteria | No Criteria |  | Uo - No Criteria
4 | Cadmium b | 1.6269 | Y |  |  | 0.2 |  | 0.2 | MEC<C, go to Step 5 |  | Y |  |  | 0.1268 |  | B<C, Step 7
5a | Chromium (III) | 134.3574 | Y | N |  | 2.86 |  | 2.86 | MEC<C, go to Step 5 | [6 empty] | No detected value of B, Step 7
5b | Chromium (VI) b | 11.4345 | Y | N |  | 1.44 |  | 1.44 | MEC<C, go to Step 5 |  | Y |  |  | 4.4 |  | B<C, Step 7
6 | Copper c | 3.7349 | Y | N |  | 6.73 |  | 6.73 | Y |  | Y |  |  | 2.45 |  | B<C, Step 7 |  | Y | MEC => C [6.730 ug/l vs 3.735 ug/l ] | 24.5157 | 12.7341
7 | Lead b | 1.6253 | Y | N |  | 2.68 |  | 2.68 | Y |  | Y |  |  | 0.8 |  | B<C, Step 7 |  | Y | MEC => C [2.680 ug/l vs 1.625 ug/l ] | 14.8714 | 7.4128
8 | Mercury (303d listed) b | 0.025 | Y | N |  | 0.11 |  | 0.11 | Y |  | Y |  |  | 0.0086 |  | B<C, Step 7 |  | Y | MEC => C [0.110 ug/l vs 0.025 ug/l ] | 0.046224 | 0.017174
9 | Nickel b | 8.2828 | Y | N |  | 37.8 |  | 37.8 | Y |  | Y |  |  | 3.7 |  | B<C, Step 7 |  | Y | MEC => C [37.800 ug/l vs 8.283 ug/l ] | 66.1032 | 45.0146
10 | Selenium (303d listed) b | 5 | Y | N |  | 22.1 |  | 22.1 | Y |  | Y |  |  | 0.39 |  | B<C, Step 7 |  | Y | MEC => C [22.100 ug/l vs 5.000 ug/l ] | 7.3858 | 4.35
11 | Silver b | 1.0674 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y |  |  | 0.0516 |  | B<C, Step 7
12 | Thallium | 6.3 | Y | N |  | 1.46 |  | 1.46 | MEC<C, go to Step 5 |  | Y |  |  | 0.21 |  | B<C, Step 7
13 | Zinc b | 76.623 | Y | N |  | 50.41 |  | 50.41 | MEC<C, go to Step 5 |  | Y |  |  | 5.1 |  | B<C, Step 7
14 | Cyanide b | 1 | Y | N |  | 4.8 |  | 4.8 | Y |  | Y | Y | 0.4 |  | FALSE | No detected value of B, Step 7 |  | Y | MEC => C [4.800 ug/l vs 1.000 ug/l ] | 6.4 | 3.6502
15 | Asbestos | No Criteria |  |  |  |  | No Criteria |  | No Criteria | [6 empty] | No Criteria | No Criteria |  | Uo - No Criteria
16 | 2,3,7,8-TCDD | 1.4e-08 | Y | Y | 3.6e-07 | [5 empty] | Y |  | 3.5e-07 |  |  | No detected value of B, Step 7
B: dioxin-TEQ (303d listed); Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) C: 1.4e-08; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) D: Y; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) E: Y; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) H: MDL > C, Interim Monitor, Go To Step 5; Y if If MEC >= C, effluent limitation is required; 2. If MEC<C, go to Step 5 L: Y; Y if If MEC >= C, effluent limitation is required; 2. If MEC<C, go to Step 5 O: 7.1e-08; If B>C, effluent limitation is required Q: Y; If B>C, effluent limitation is required r: Y; RPA Result S: Y; Reason T: Trigger 3 | 2.8087e-08 | 1.4e-08
17 | Acrolein | 780 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
18 | Acrylonitrile | 0.66 | Y | Y | 2 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.03 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
19 | Benzene | 71 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
20 | Bromoform | 360 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
21 | Carbon Tetrachloride | 4.4 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y |  |  | 0.06 |  | B<C, Step 7
22 | Chlorobenzene | 21000 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
23 | Chlorodibromomethane | 34 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
24 | Chloroethane | No Criteria | Y | y | 0.5 |  | No Criteria | 0.5 | No Criteria |  | Y | Y | 0.5 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
25 | 2-Chloroethylvinyl ether | No Criteria | Y | Y | 0.5 |  | No Criteria | 0.5 | No Criteria |  | Y | Y | 0.5 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
26 | Chloroform | No Criteria | Y | N |  | 0.9 | No Criteria | 0.9 | No Criteria |  | Y | Y | 0.5 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
27 | Dichlorobromomethane | 46 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
28 | 1,1-Dichloroethane | No Criteria | Y | Y | 0.5 |  | No Criteria | 0.5 | No Criteria |  | Y | Y | 0.05 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
29 | 1,2-Dichloroethane | 99 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y |  |  | 0.04 |  | B<C, Step 7
30 | 1,1-Dichloroethylene | 3.2 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
31 | 1,2-Dichloropropane | 39 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
32 | 1,3-Dichloropropylene | 1700 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 | [6 empty] | No detected value of B, Step 7
33 | Ethylbenzene | 29000 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
34 | Methyl Bromide | 4000 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
35 | Methyl Chloride | No Criteria | Y | Y | 0.5 |  | No Criteria | 0.5 | No Criteria |  | Y | Y | 0.5 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
36 | Methylene Chloride | 1600 | Y | N |  | 2 |  | 2 | MEC<C, go to Step 5 |  | Y |  |  | 0.5 |  | B<C, Step 7
37 | 1,1,2,2-Tetrachloroethane | 11 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
38 | Tetrachloroethylene | 8.85 | Y | N |  | 0.5 |  | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
39 | Toluene | 200000 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
40 | 1,2-Trans-Dichloroethylene | 140000 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
41 | 1,1,1-Trichloroethane | No Criteria | Y | Y | 0.5 |  | No Criteria | 0.5 | No Criteria |  | Y | Y | 0.5 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
42 | 1,1,2-Trichloroethane | 42 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.05 |  | FALSE | No detected value of B, Step 7
43 | Trichloroethylene | 81 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
44 | Vinyl Chloride | 525 | Y | Y | 0.5 |  | MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
45 | 2-Chlorophenol | 400 | Y | Y | 2 |  | MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 1.2 |  | FALSE | No detected value of B, Step 7
46 | 2,4-Dichlorophenol | 790 | Y | Y | 1 |  | MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 1.3 |  | FALSE | No detected value of B, Step 7
47 | 2,4-Dimethylphenol | 2300 | Y | Y | 2 |  | MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 1.3 |  | FALSE | No detected value of B, Step 7
48 | 2-Methyl- 4,6-Dinitrophenol | 765 | Y | Y | 5 |  | MDL<=C, MDL=MEC | 5 | MEC<C, go to Step 5 |  | Y | Y | 1.2 |  | FALSE | No detected value of B, Step 7
49 | 2,4-Dinitrophenol | 14000 | Y | Y | 5 |  | MDL<=C, MDL=MEC | 5 | MEC<C, go to Step 5 |  | Y | Y | 0.7 |  | FALSE | No detected value of B, Step 7
50 | 2-Nitrophenol | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 1.3 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
51 | 4-Nitrophenol | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 1.6 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
52 | 3-Methyl 4-Chlorophenol | No Criteria | Y | Y | 1 |  | No Criteria | 1 | No Criteria |  | Y | Y | 1.1 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
53 | Pentachlorophenol | 7.9 | Y | Y | 1 |  | MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 1 |  | FALSE | No detected value of B, Step 7
54 | Phenol | 4600000 | Y | Y | 1 |  | MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 1.3 |  | FALSE | No detected value of B, Step 7
55 | 2,4,6-Trichlorophenol | 6.5 | Y | N |  | 5 |  | 5 | MEC<C, go to Step 5 |  | Y | Y | 1.3 |  | FALSE | No detected value of B, Step 7
56 | Acenaphthene | 2700 | Y | Y | 0.3 |  | All ND MDL<=C, MDL=MEC | 0.3 | MEC<C, go to Step 5 |  | Y |  |  | 0.0015 |  | B<C, Step 7
57 | Acenaphthylene | No Criteria | Y | Y | 0.2 |  | No Criteria | 0.2 | No Criteria |  | Y |  |  | 0.00053 |  | No Criteria | No Criteria |  | Uo - No Criteria
58 | Anthracene | 110000 | Y | Y | 0.3 |  | All ND MDL<=C, MDL=MEC | 0.3 | MEC<C, go to Step 5 |  | Y |  |  | 0.0005 |  | B<C, Step 7
59 | Benzidine | 0.00054 | Y | Y | 5 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y | Y | 0.0015 |  | Y | No detected value of B, Step 7 |  |  | Effluent MDL > C, Interim Monitor
60 | Benzo(a)Anthracene | 0.049 | Y | Y | 0.1 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.0053 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
61 | Benzo(a)Pyrene | 0.049 | Y | Y | 0.3 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.00029 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
62 | Benzo(b)Fluoranthene | 0.049 | Y | Y | 0.3 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.0046 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
63 | Benzo(ghi)Perylene | No Criteria | Y | Y | 0.3 |  | No Criteria | 0.3 | No Criteria |  | Y |  |  | 0.0027 |  | No Criteria | No Criteria |  | Uo - No Criteria
64 | Benzo(k)Fluoranthene | 0.049 | Y | Y | 0.3 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.0015 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
65 | Bis(2-Chloroethoxy)Methane | No Criteria | Y | Y | 2 |  | No Criteria | 2 | No Criteria |  | Y | Y | 0.3 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
66 | Bis(2-Chloroethyl)Ether | 1.4 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
67 | Bis(2-Chloroisopropyl)Ether | 170000 | Y | Y | 2 |  | All ND MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 | [6 empty] | No detected value of B, Step 7
68 | Bis(2-Ethylhexyl)Phthalate | 5.9 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
69 | 4-Bromophenyl Phenyl Ether | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 0.23 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
70 | Butylbenzyl Phthalate | 5200 | Y | Y | 2 |  | All ND MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 0.52 |  | FALSE | No detected value of B, Step 7
71 | 2-Chloronaphthalene | 4300 | Y | Y | 2 |  | All ND MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
72 | 4-Chlorophenyl Phenyl Ether | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 0.3 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
73 | Chrysene | 0.049 | Y | Y | 0.3 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.0024 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
74 | Dibenzo(a,h)Anthracene | 0.049 | Y | Y | 0.1 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.00064 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
75 | 1,2-Dichlorobenzene | 17000 | N |  |  | 0 | No Effluent Data |  |  |  | Y | Y | 0.8 |  | FALSE | No detected value of B, Step 7
76 | 1,3-Dichlorobenzene | 2600 | Y | Y | 0.5 |  | All ND MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.8 |  | FALSE | No detected value of B, Step 7
77 | 1,4-Dichlorobenzene | 2600 | Y | Y | 0.5 |  | All ND MDL<=C, MDL=MEC | 0.5 | MEC<C, go to Step 5 |  | Y | Y | 0.8 |  | FALSE | No detected value of B, Step 7
78 | 3,3 Dichlorobenzidine | 0.077 | Y | Y | 5 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y | Y | 0.001 |  | FALSE | No detected value of B, Step 7 |  |  | Effluent MDL > C, Interim Monitor
79 | Diethyl Phthalate | 120000 | Y | Y | 2 |  | All ND MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 0.24 |  | FALSE | No detected value of B, Step 7
80 | Dimethyl Phthalate | 2900000 | Y | Y | 2 |  | All ND MDL<=C, MDL=MEC | 2 | MEC<C, go to Step 5 |  | Y | Y | 0.24 |  | FALSE | No detected value of B, Step 7
81 | Di-n-Butyl Phthalate | 12000 | Y | Y | 5 |  | All ND MDL<=C, MDL=MEC | 5 | MEC<C, go to Step 5 |  | Y | Y | 0.5 |  | FALSE | No detected value of B, Step 7
82 | 2,4-Dinitrotoluene | 9.1 | Y | Y | 5 |  | All ND MDL<=C, MDL=MEC | 5 | MEC<C, go to Step 5 |  | Y | Y | 0.27 |  | FALSE | No detected value of B, Step 7
83 | 2,6-Dinitrotoluene | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 0.29 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
84 | Di-n-Octyl Phthalate | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 0.38 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
85 | 1,2-Diphenylhydrazine | 0.54 | Y | Y | 1 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.0037 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
86 | Fluoranthene | 370 | Y | Y | 0.05 |  | All ND MDL<=C, MDL=MEC | 0.05 | MEC<C, go to Step 5 |  | Y |  |  | 0.011 |  | B<C, Step 7
87 | Fluorene | 14000 | Y | Y | 0.1 |  | All ND MDL<=C, MDL=MEC | 0.1 | MEC<C, go to Step 5 |  | Y |  |  | 0.00208 |  | B<C, Step 7
88 | Hexachlorobenzene | 0.00077 | Y | Y | 0.1 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 2.02e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
89 | Hexachlorobutadiene | 50 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
90 | Hexachlorocyclopentadiene | 17000 | Y | Y | 5 |  | All ND MDL<=C, MDL=MEC | 5 | MEC<C, go to Step 5 |  | Y | Y | 0.31 |  | FALSE | No detected value of B, Step 7
91 | Hexachloroethane | 8.9 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.2 |  | FALSE | No detected value of B, Step 7
92 | Indeno(1,2,3-cd)Pyrene | 0.049 | Y | Y | 0.05 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.004 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
93 | Isophorone | 600 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
94 | Naphthalene | No Criteria | Y | Y | 0.2 |  | No Criteria | 0.2 | No Criteria |  | Y |  |  | 0.0023 |  | No Criteria | No Criteria |  | Uo - No Criteria
95 | Nitrobenzene | 1900 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.25 |  | FALSE | No detected value of B, Step 7
96 | N-Nitrosodimethylamine | 8.1 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.3 |  | FALSE | No detected value of B, Step 7
97 | N-Nitrosodi-n-Propylamine | 1.4 | Y | Y | 5 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y | Y | 0.001 |  | FALSE | No detected value of B, Step 7 |  |  | Effluent MDL > C, Interim Monitor
98 | N-Nitrosodiphenylamine | 16 | Y | Y | 1 |  | All ND MDL<=C, MDL=MEC | 1 | MEC<C, go to Step 5 |  | Y | Y | 0.001 |  | FALSE | No detected value of B, Step 7
99 | Phenanthrene | No Criteria | Y | Y | 0.05 |  | No Criteria | 0.05 | No Criteria |  | Y |  |  | 0.0061 |  | No Criteria | No Criteria |  | Uo - No Criteria
100 | Pyrene | 11000 | Y | Y | 0.05 |  | All ND MDL<=C, MDL=MEC | 0.05 | MEC<C, go to Step 5 |  | Y |  |  | 0.0051 |  | B<C, Step 7
101 | 1,2,4-Trichlorobenzene | No Criteria | Y | Y | 5 |  | No Criteria | 5 | No Criteria |  | Y | Y | 0.3 |  | FALSE | No Criteria | No Criteria |  | Uo - No Criteria
102 | Aldrin | 0.00014 | Y | Y | 0.005 |  | MDL > C, Interim Monitor, Go To Step 5 | [8 empty] | No detected value of B, Step 7 |  |  | Effluent MDL > C, Interim Monitor
103 | alpha-BHC | 0.013 | Y | Y | 0.01 |  | All ND MDL<=C, MDL=MEC | 0.01 | MEC<C, go to Step 5 |  | Y |  |  | 0.000496 |  | B<C, Step 7
104 | beta-BHC | 0.046 | Y | Y | 0.005 |  | All ND MDL<=C, MDL=MEC | 0.005 | MEC<C, go to Step 5 |  | Y |  |  | 0.000413 |  | B<C, Step 7
105 | gamma-BHC | 0.063 | Y | Y | 0.01 |  | All ND MDL<=C, MDL=MEC | 0.01 | MEC<C, go to Step 5 |  | Y |  |  | 0.0007034 |  | B<C, Step 7
106 | delta-BHC | No Criteria | Y | Y | 0.01 |  | No Criteria | 0.01 | No Criteria |  | Y |  |  | 4.2e-05 |  | No Criteria | No Criteria |  | Uo - No Criteria
107 | Chlordane (303d listed) | 0.00059 | Y | Y | 0.02 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.00018 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
108 | 4,4'-DDT (303d listed) | 0.00059 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 6.6e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
109 | 4,4'-DDE (linked to DDT) | 0.00059 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.000693 |  |  |  |  | Effluent MDL > C, Interim Monitor
110 | 4,4'-DDD | 0.00084 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.000313 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
111 | Dieldrin (303d listed) | 0.00014 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 0.000264 |  |  |  |  | Effluent MDL > C, Interim Monitor
112 | alpha-Endosulfan | 0.0087 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 3.1e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
113 | beta-Endolsulfan | 0.0087 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 6.9e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
114 | Endosulfan Sulfate | 240 | Y | Y | 0.01 |  | All ND MDL<=C, MDL=MEC | 0.01 | MEC<C, go to Step 5 |  | Y |  |  | 8.19e-05 |  | B<C, Step 7
115 | Endrin | 0.0023 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 3.6e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
116 | Endrin Aldehyde | 0.81 | Y | Y | 0.01 |  | All ND MDL<=C, MDL=MEC | 0.01 | MEC<C, go to Step 5 | [6 empty] | No detected value of B, Step 7
117 | Heptachlor | 0.00021 | Y | Y | 0.01 |  | MDL > C, Interim Monitor, Go To Step 5 |  |  |  | Y |  |  | 1.9e-05 |  | B<C, Step 7 |  |  | Effluent MDL > C, Interim Monitor
118 | Heptachlor Epoxide | 0.00011 | Y | N |  | 0.1 |  | 0.1 | Y |  | Y |  |  | 2.458e-05 |  | B<C, Step 7 |  | Y | MEC => C [0.100000 ug/l vs 0.000110 ug/l ]
A: 119-125; B: PCBs sum (2); Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) C: 0.00017; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) D: Y; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) E: N; Lowest (most stringent) Criteria (Enter "No Criteria" for no criteria) G: 0.000651; (MEC= deteted max value; if all ND & MDL<C then MEC = MDL) I: 0.000651; Y if If MEC >= C, effluent limitation is required; 2. If MEC<C, go to Step 5 J: Y; If B>C, effluent limitation is required Q: No detected value of B, Step 7; RPA Result S: Y; Reason T: MEC => C [0.000651 ug/l vs 0.000170 ug/l ] | 0.0034105 | 0.0017
126 | Toxaphene | 0.0002 | Y | Y | 0.05 |  | MDL > C, Interim Monitor, Go To Step 5 | [8 empty] | No detected value of B, Step 7 |  |  | Effluent MDL > C, Interim Monitor
| Tributylin | 0.01 |  |  |  |  | No Effluent Data |  |  |  | Y | Y | 0.001 |  | FALSE | No detected value of B, Step 7 |  |  | Ud-No Effluent Data
| Total PAHs | 15 | Y | Y | 0.1 |  | All ND MDL<=C, MDL=MEC | 0.1 | MEC<C, go to Step 5 |  | Y |  |  | 0.26 | B MDLs>C, Monitoring Required | B<C, Step 7 | 0
a. The most stringent of salt and fresh water criteria were selected for this analysis.
b. According to Table 1 of Section (b)(1) of CTR (40CFR 131.38), those criteria should use Basin Plan objectives; criteria for Se and CN are specified by the NTR.
c. Criteria for copper is taken from CTR. CTR criteria for copper is expressed as dissolved metals. The copper criter in the table is adjusted by dividing a factor of 0.83 to convert the dissovled to total metal concetration.
The freshwater criteria for Selenium is taken from NTR.
| d. Acronyms in the "Final Result" column: |  | Ud: Cannot determine reasonable potential due to the absence of data, or because Minimum DL is greater than water quality objective or CTR criteria
Uo: No criteria available
IM: Interim monitoring is required
Note on W11: Ken Katen: Applies to this permit only per Richard Looker. Future shallow water discharger translators to be worked out through regionwide policy decisions if possible.
Top left corner of inserted data goes here. Data MUST be in two-column format ("<" if ND in left column, data or detection limit in right column).

## WQBELs
Data Initialization: |  | Dilution: | 9 | 0
|  | No. Samples Per Month: | 4
[23 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
[6 empty] | Enter By Hand |  |  |  | Enter These Values By Hand | [8 empty] | Hand Enter
Beginning |  |  | Aquatic Criteria Available? (Min. if Y) | Site Specific Translators? | Human Health Criteria Available? | Bioaccum- ulative? | Human Carcinogen? (Y/N -Only Fill in Y's) | Applicable Acute WQO | Applicable Chronic WQO | Number of Quantified Data | Max. Quantified Data | Min. Quantified Data | Number of NDs | Min DL | Average, Quantified Data | Standard Deviation, Quantified Data | Percent NDs. | Bckkgrnd Data Available? | Average Background Data | Acute ECA | Chronic ECA | Human Health ECA | CV, by SIP Guidance | Acute ECA (Sigma^2) | Acute ECA Sigma | Chronic ECA (Sigma^2) | Chronic ECA Sigma | Acute ECA Multiplier | Chronic ECA Multiplier | Acute LTA | Chronic LTA | AMEL Sigma^2 | AMEL Sigma | MDEL Multiplier | AMEL Multiplier | MDEL | AMEL | MDEL Human Health | AMEL Human Health | Daily Maximum | Monthly Average
| Constituent name | [16 empty] | Max If Avail.
RP?
A | B | C | D | E | F | G | H | I | J | K | L | M | N | O | P | Q | R | S | T | U | V | W | X | Y | Z | AA | AB | AC | AD | AE | AF | AG |  |  | AH | AI | AJ | AK | AL | AM | AN
1 | Antimony
2 | Arsenic b
3 | Beryllium
4 | Cadmium b
5a | Chromium (III)
5b | Chromium (VI) b
6 | Copper c | Y | 3.7349 |  | N |  |  | 5.7831 | 3.7349 | 112 | 20 | 0.8 | 0 | 0.5 | 5.11 | 2.54 | 0 | 2.45 |  | 35.7813 | 15.2994 | No HH Criteria | 0.54894 | 0.26339 | 0.51321 | 0.072631 | 0.2695 | 0.34575 | 0.55403 | 12.3713 | 8.4763 | 0.072631 | 0.2695 | 2.8923 | 1.5023 | 24.5157 | 12.7341 |  |  | 24.5157 | 12.7341
7 | Lead b | Y | 1.6253 |  | N |  |  | 41.7085 | 1.6253 | 20 | 3.5 | 0.46 | 1 | 0.1 | 1.04 | 0.68 | 0.047619 | 0.8 |  | 409.8851 | 9.0532 | No HH Criteria | 0.6 | 0.30748 | 0.55451 | 0.086178 | 0.29356 | 0.32108 | 0.52743 | 131.6072 | 4.775 | 0.086178 | 0.29356 | 3.1145 | 1.5524 | 14.8714 | 7.4128 |  |  | 14.8714 | 7.4128
8 | Mercury (303d listed) b | Y | 0.025 |  | 0.051 |  |  | 2.1 | 0.025 | 41 | 0.0375 | 0.0016 | 2 | 0.5 | 7.82 | 6.28 | 0.046512 | 0.0086 |  | 2.1 | 0.025 | 0.051 | 1.192 | 0.88415 | 0.94029 | 0.30397 | 0.55134 | 0.17464 | 0.3229 | 0.36674 | 0.0080724 | 0.30397 | 0.55134 | 5.7262 | 2.1275 | 0.046224 | 0.017174 | 0.13726 | 0.051 | 0.046224 | 0.017174
9 | Nickel b | Y | 8.2828 |  | 4600 |  |  | 74.7475 | 8.2828 | 159 | 87 | 0.5 | 1 | 0.5 | 15.23 | 7.37 | 0.00625 | 3.7 |  | 714.1747 | 49.5283 | 45966.7 | 0.28202 | 0.076531 | 0.27664 | 0.019689 | 0.14032 | 0.54596 | 0.72867 | 389.9122 | 36.0898 | 0.019689 | 0.14032 | 1.8316 | 1.2473 | 66.1032 | 45.0146 | 67501.2386 | 45966.7 | 66.1032 | 45.0146
10 | Selenium (303d listed) b | Y | 5 |  | N |  |  | 20 | 5 | 158 | 41 | 3.6 | 2 | 0.5 | 11.26 | 5.57 | 0.0125 | 0.39 |  | 20 | 5 | No HH Criteria | 0.41334 | 0.15773 | 0.39715 | 0.041825 | 0.20451 | 0.4296 | 0.63459 | 8.5919 | 3.1729 | 0.041825 | 0.20451 | 2.3278 | 1.371 | 7.3858 | 4.35 |  |  | 7.3858 | 4.35
11 | Silver b
12 | Thallium | [8 empty] | 2 | 13 | 0.2 | 13 | 0.1 |  |  | 0.86667
13 | Zinc b
14 | Cyanide b | Y | 1 |  | 220000 |  |  | 1 | 1 | 6 | 14 | 10 | 107 | 10 |  |  | 0.9469 | 0.4 |  | 6.4 | 6.4 | 2199996.4 | 0.44563 | 0.18115 | 0.42561 | 0.048454 | 0.22012 | 0.40681 | 0.61399 | 2.6036 | 3.9295 | 0.048454 | 0.22012 | 2.4581 | 1.402 | 6.4 | 3.6502 | 3857348.2866 | 2199996.4 | 6.4 | 3.6502
15 | Asbestos
16 | 2,3,7,8 TCDD
B: dioxin-TEQ (303d listed); RP? C: Y; RP? F: 1.4e-08; RP? I: No Acute; RP? J: No Chronic; RP? K: 3; RP? L: 4.2e-07; RP? R: 0; RP? S: 7.1e-08; RP? W: 1.4e-08; RP? X: 0.6; RP? Y: 0.30748; RP? Z: 0.55451; RP? AA: 0.086178; RP? AB: 0.29356; RP? AC: 0.32108; RP? AD: 0.52743; RP? AG: 0.086178 | 0.29356 | 3.1145 | 1.5524 | 0 | 0 | 2.8087e-08 | 1.4e-08 | 0 | 0
17 | Acrolein
18 | Acrylonitrile
19 | Benzene
20 | Bromoform
21 | Carbon Tetrachloride
22 | Chlorobenzene
23 | Chlorodibromomethane
24 | Chloroethane
25 | 2-Chloroethylvinyl ether
26 | Chloroform
27 | Dichlorobromomethane
28 | 1,1-Dichloroethane
29 | 1,2-Dichloroethane
30 | 1,1-Dichloroethylene
31 | 1,2-Dichloropropane
32 | 1,3-Dichloropropylene
33 | Ethylbenzene
34 | Methyl Bromide
35 | Methyl Chloride
36 | Methylene Chloride
37 | 1,1,2,2-Tetrachloroethane
38 | Tetrachloroethylene
39 | Toluene
40 | 1,2-Trans-Dichloroethylene
41 | 1,1,1-Trichloroethane
42 | 1,1,2-Trichloroethane
43 | Trichloroethylene
44 | Vinyl Chloride
45 | 2-Chlorophenol
46 | 2,4-Dichlorophenol
47 | 2,4-Dimethylphenol
48 | 2-Methyl- 4,6-Dinitrophenol
49 | 2,4-Dinitrophenol
50 | 2-Nitrophenol
51 | 4-Nitrophenol
52 | 3-Methyl 4-Chlorophenol
53 | Pentachlorophenol
54 | Phenol
55 | 2,4,6-Trichlorophenol
56 | Acenaphthene
57 | Acenaphthylene
58 | Anthracene
59 | Benzidine
60 | Benzo(a)Anthracene
61 | Benzo(a)Pyrene
62 | Benzo(b)Fluoranthene
63 | Benzo(ghi)Perylene
64 | Benzo(k)Fluoranthene
65 | Bis(2-Chloroethoxy)Methane
66 | Bis(2-Chloroethyl)Ether
67 | Bis(2-Chloroisopropyl)Ether
68 | Bis(2-Ethylhexyl)Phthalate
69 | 4-Bromophenyl Phenyl Ether
70 | Butylbenzyl Phthalate
71 | 2-Chloronaphthalene
72 | 4-Chlorophenyl Phenyl Ether
73 | Chrysene
74 | Dibenzo(a,h)Anthracene
75 | 1,2-Dichlorobenzene
76 | 1,3-Dichlorobenzene
77 | 1,4-Dichlorobenzene
78 | 3,3 Dichlorobenzidine
79 | Diethyl Phthalate
80 | Dimethyl Phthalate
81 | Di-n-Butyl Phthalate
82 | 2,4-Dinitrotoluene
83 | 2,6-Dinitrotoluene
84 | Di-n-Octyl Phthalate
85 | 1,2-Diphenylhydrazine
86 | Fluoranthene
87 | Fluorene
88 | Hexachlorobenzene
89 | Hexachlorobutadiene
90 | Hexachlorocyclopentadiene
91 | Hexachloroethane
92 | Indeno(1,2,3-cd)Pyrene
93 | Isophorone
94 | Naphthalene
95 | Nitrobenzene
96 | N-Nitrosodimethylamine
97 | N-Nitrosodi-n-Propylamine
98 | N-Nitrosodiphenylamine
99 | Phenanthrene
100 | Pyrene
101 | 1,2,4-Trichlorobenzene
102 | Aldrin
103 | alpha-BHC
104 | beta-BHC
105 | gamma-BHC
106 | delta-BHC
107 | Chlordane (303d listed)
108 | 4,4'-DDT (303d listed)
109 | 4,4'-DDE (linked to DDT) | [8 empty] | 0 |  |  | 3 | 0.01 |  |  | 1
110 | 4,4'-DDD
111 | Dieldrin (303d listed) | [8 empty] | 0 |  |  | 3 | 0.01 |  |  | 1
112 | alpha-Endosulfan
113 | beta-Endolsulfan
114 | Endosulfan Sulfate
115 | Endrin
116 | Endrin Aldehyde
117 | Heptachlor
118 | Heptachlor Epoxide | Y | 0.0036 |  | 0.00011 |  |  | 0.053 | 0.0036 | [8 empty] | 2.458e-05 |  | 0.52978 | 0.035779 | 0.00087878 | 0.6 | 0.30748 | 0.55451 | 0.086178 | 0.29356 | 0.32108 | 0.52743 | 0.1701 | 0.018871 | 0.086178 | 0.29356 | 3.1145 | 1.5524 | 0.058773 | 0.029296 | 0.001763 | 0.00087878
A: 119-125; B: PCBs sum (2); RP? C: Y; RP? D: 0.014; RP? F: 0.00017; RP? I: No Acute; RP? J: 0.014; RP? S: N; RP? V: 0.14; RP? W: 0.0017; RP? X: 0.6; RP? Y: 0.30748; RP? Z: 0.55451; RP? AA: 0.086178; RP? AB: 0.29356; RP? AC: 0.32108; RP? AD: 0.52743; RP? AF: 0.073841; RP? AG: 0.086178 | 0.29356 | 3.1145 | 1.5524 | 0.22997 | 0.11463 | 0.00034105 | 0.00017
126 | Toxaphene
Tributylin
Total PAHs
Top left corner of inserted data goes here. Data MUST be in two-column format ("<" if ND in left column, data or detection limit in right column).