## 045_SSO
Tracking No. | Regional Board Contact Notified (Name, or "VOICE MAIL", or "FAX") | Date & Time Reported | Reported By | Phone No. | Reporting Agency | Responsible Agency | Start Date & Time | End Date & Time | Estimated Overflow Flow Rate (gallons per minute) | Total Overflow Volume (Gallons) | Overflow Volume Recovered (Gallons) | Overflow Volume Released to Environment (Gallons) | SSO Location -- Street Address | SSO Location -- City | SSO Zip Code | SSO County (SD, RV, OR) | SSO Structure I.D. | No. of Overflows within 1000 ft. of this location in past 12 months | Dates of Overflows within 1000 ft. of this location in past 12 months | SSO Cause - Short Description | SSO Cause (Detailed Description) | SSO Correction and Prevention | 72-hour period measurable precipitation? (Y or N) | Entered Storm Drain? (Y or N) | Reached surface waters other than storm drain? (Y or N) | Initial Receiving Waters | Secondary Receiving Waters | Final Sewage Destination | Local Health Services Agency Notified (Y or N) | OES Notified (Y or N) | Warning signs posted | Location of Posting | No. of Days Signs Posted | Remarks | Private | Place an "P", "R", "S", "O" here if it is a Plant, Recycled, Secondary, or Other non SSO
045022 | faxed | 2004-12-16 14:35 | Robert Milam | 760.726-1340 | Buena Sanitation District | Buena Sanitation District | 2004-12-16 07:42 | 2004-12-16 08:05 | 5 | 115 | 115 | 0 | 1831 Anna Lane | Vista | 92083 | SD | PRIVATE LATERAL | 0 | N/A | Roots | Private lateral contained large root mass which protruded from within the lateral line into the mainline causing the blockage | Chain flailed line to remove root mass then televised line to ascertain problem. Put line on a routine hot spot list. | N | N | N | Small local drainage ditch | Dry field (vacuumed up) | Vacuumed up from dry field | Y | N/A | N | Along drainage area | 2 | This overflow was captured quickly after the start and cleared up and completely washed down and removed
040501 | Clay Clifton | 07/27/04 - 8:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-07-26 21:00 | 2004-07-26 22:00 | 5 | 300 | 300 | 0 | 5980 Avenida Encinas | Carlsbad | 92008 | SD | Property Line Cleanout | 0 | N/A | GREASE | Grease clogged lateral | More aggressive cleaning program | N | Y | Y | Drainage canal | Cannon Lake | Storm drain comes out to canal | Y | N | N | N/A | 0 | None | x
040502 | Clay Clifton | 08/26/04 - 9:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-08-25 15:00 | 2004-08-25 18:00 | 1 | 180 | 180 | 0 | 2515 El Camino Real | Carlsbad | 92008 | SD | Private lateral stoppage-cleanout | 0 | N/A | Unknown | Private lateral coming from Restaurant had blockage that caused overflow. (China Buffet) | The Restaurant must do regular cleaning of their lateral | N | N | N | None | None | Our crew recaptured all of the overflow and the washdown water | Y | N | N | N/A | 0 | None | x
040503 | Clay Clifton | 9/30/04 - 15:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-09-27 15:00 | 2004-09-27 15:15 | 1 | 15 | 15 | 0 | 2520 El Camino Real | Carlsbad | 92008 | SD | Private stoppage in Parking lot | 0 | N/A | Unknown | Private stoppage in shopping center parking lot | Shopping center management company should do regular preventative maintenance | N | N | N | Buena Vista Creek | Buena Vista Lagoon | Recaptured before M34 | Y | N | N | N/A | 0 | Private Stoppage | x
040504 | Clay Clifton | 10/07/04 - 3:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-10-07 09:50 | 2004-10-07 11:30 | 5 | 50 | 30 | 20 | 393 Oak | Carlsbad | 92008 | SD | 6 inch lateral cleanout | 0 | N/A | ROOTS | Roots in lateral | Rodded 6 inch lateral cleared stoppage. Vacuumed up twenty galls of spill. | N | N | N | None | None | Railroad easement | N | N | N | N/A | 0 | This was hard to give a gpm because it was not a constant flow
040506 | Clay Clifton | 10/28/04 - 5:45 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-10-28 17:45 | 2004-10-28 18:00 | 0.67 | 10 | 10 | 0 | 1519 Chestnut | Carlsbad | 92008 | SD | 3 inch cleanout | 0 | N/A | ROOTS | Sewer main backup, flow came out of 3 inch cleanout at house and toilet in house | Areas cleaned up. All overflow of sewage captured. Areas disinfected. | Y | N | N | None | None | None | Y | N | N | N/A | 0 | None
040508 | Clay Clifton | 11/03/04 - 10:30 | Don Wasko | 760-438-2723 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-11-02 15:00 | 2004-11-02 15:25 | 25 | 625 | 625 | 0 | Aviara Pkwy/Palomar Airport Rd | Carlsbad | 92008 | SD | Manhole | 0 | N/A | VANDALISM | Vandalism-rocks in manhole caused overflow | Routine cleaning and system surveillance | N | Y | Y | Encinas Creek | Encinas Creek | We recaptured on Encinas Creek at Hidden Valley Rd | Y | N | Y | 200 yds North/South of mouth of Encinas Creek. By order of Clay Clifton-County Health | 2 | Samples taken about 3:30 pm on 11/2/04 mouth of Encinas Creek
040510 | Clay Clifton | 12/8/04 - 14:00 | Don Wasko | 760-438-2725 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-12-07 11:45 | 2004-12-07 12:30 | 15 | 225 | 450 | 450 | Cove Drive | Carlsbad | 92008 | SD | 1 inch cleanout lid. | 0 | N/A | PUMP STATION FAILURE | UPS failure and time delay | Replaced time delay and UPS has been removed. Station has stand-by generator if power is interrupted | Y | N | Y | Agua Hedionda Lagoon | None | None | Y | N | Y | End of Cove Dr and Snug Harbor, Fox's Landing | 3 | None
040509 | Clay Clifton | 12/07/04 - 12:25 | Don Wasko | 760-438-2724 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-12-07 12:25 | 2004-12-07 12:26 | 10 | 10 | 0 | 10 | 6830 Ave Encinas | Carlsbad | 92008 | SD | Property line cleanout | 0 | N/A | ROOTS | Roots in lateral caused back up | Excavate to replace section of pipe that has roots | Y | N | N | None | None | On the property, soaked into grass area | Y | N | N | N/A | 0 | None
040511 | Clay Clifton | 01/03/05 - 14:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-01-02 22:00 | 2005-01-02 22:30 | 1 | 30 | 30 | 0 | 260 Hemlock | Carlsbad | 92008 | SD | Toilet inside residence | 0 | N/A | UNKNOWN | Blockage in city main caused backup into house | We need to televise the main to determine cause | Y | N | N | None | None | Backed up into residence | Y | N | N | N/A | 0 | None
040512 | Clay Clifton | 01/10/05 - 8:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-01-09 13:00 | 2005-01-09 14:00 | 1 | 60 | 60 | 0 | 418 Chinquapin Dr | Carlsbad | 92008 | SD | 4 inch cleanout in backyard | 1 | 38074 | UNKNOWN | We will televise the main to determine the cause | Vactored and cleared and cleaned sewer main | Y | N | N | None | None | Lawn area of backyard | Y | N | N | N/A | 0 | None
040513 | Clay Clifton | 02/22/05 - 9:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-02-19 11:45 | 2005-02-19 13:15 | 10 | 900 | 0 | 900 | Marron Rd/Monroe ST | Carlsbad | 92008 | SD | Manhole | 0 | N/A | GREASE | Unknown, will televise to determine cause. | Vactored line in main | Y | Y | N | None | None | Buena Vista Lagoon | Y | N | N | N/A | 0 | None
040514 | Clay Clifton | 02/24/05 - 15:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-02-23 17:20 | 2005-02-23 17:20 | 15 | 15 | 15 | 0 | 4513 Cove Drive | Carlsbad | 92008 | SD | 6 inch lateral | 1 | 38328 | POWER FAILURE | We think that there was a very quick power outage that occurred at the pump station. This caused one of the main controllers fuses to blow. We replaced the fuse within 25 minutes of the alarm call. This caused the gravity line to back up and spill into an underground parking area. As one of the crew members arrived at the site it had just begun to spill and enter a sump area that contained the spill. We got pumps running and everything back to normal. We cleaned the sump using a vacuum. | We are going to have an electrical evaluate this power supply that has a very low amp rating (2.5) and see if we can increase the fuse size to help prevent this from re-occurring. | Y | N | N | None | None | Underground parking sump pump. It was contained in the pit until we recaptured. | Y | N | N | N/A | 0 | 1) For descriptions and clarifications of all items on this form, refer to order No. 96-04 as amended, including the document entitled, "required fields fro Order No. 96-04 quarterly summary report." 2) If the sanitary sewer overflow event results in a discharge of 1,000 gallons or more, or in a discharge to surface waters, this form must be received by the regional board no later than five days after the overflow start date.
040515 | Clay Clifton | 03/30/05 - 11:00 | Don Wasko | 760-438-2723 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-03-30 08:15 | 2005-03-30 08:45 | 1 | 30 | 30 | 0 | 945 Carlsbad Village Dr | Carlsbad | 92008 | SD | Private cleanout | 0 | N/A | OTHER | Private sewer lateral in back of Albertson's overflowed. City staff recaptured the overflow and washed down the area. | N/A | Y | N | N | Recaptured in gutter | None | None | Y | N | N | N/A | 0 | None | x
040516 | Clay Clifton | 04/07/05 - 8:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-04-06 14:10 | 2005-04-06 14:40 | 1 | 30 | 30 | 0 | 574 Carlsbad Village Drive | Carlsbad | 92008 | SD | Inside Business | 0 | N/A | BLOCKAGE | Offset sewer lateral caused back-up | Construction crew is making repairs this morning - 4/7/05 | N | N | N | None | None | Inside business, vacuumed up and returned to sewer system. | Y | N | N | N/A | 0 | None | x
040517 | Clay Clifton | 04/13/05 - 4:10 | Gail Jones | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-04-12 09:05 | 2005-04-12 10:00 | 0 | 0 | 0 | 0 | 2290 Cosmos Ct | Carlsbad | 92008 | SD | Manhole | 0 | N/A | ROOTS | Root intrusion in two manhole's. Both are on an easement not accessible with a truck. They were full of roots from top to bottom. | Removed all roots from manhole's. We jetted the line and sprayed manhole's with round-up. | N | N | N | None | None | Soaked into the ground | Y | N | N | N/A | 0 | When we arrived the sewer line was not overflowing.
040518 | Clay Clifton | 04/19/05 - 8:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-04-18 13:52 | 2005-04-18 14:30 | 4 | 152 | 0 | 152 | 2261 Cosmos Court | Carlsbad | 92008 | SD | 6" property cleanout | 1 | 2005-04-12 | GREASE | Grease in 8" sewer main | Water was shut off, sewage was contained and cleaned up before entering storm drain. Main was rodded and cleared, main was cleaned and flowing properly. Main will be televised today to determine cause. | N | Y | Y | Storm drain | Brow Ditch | Storm drain | Y | N | N | N/A | 0 | Investigation showed pipe failure as the cause. Repair made on 7/7/05.
040520 | Clay Clifton | 06/09/05 - 8:30 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-06-08 11:00 | 2005-06-08 11:00 | 5 | 5 | 5 | 0 | 2424 Garfield St | Carlsbad | 92008 | SD | Cleanout | 0 | N/A | BLOCKAGE | We televised the main and found piece of plastic pipe in main | Ask customer to stop using water. Sewage was contained in the system. 4" main was rodded and cleared, main was cleaned and flowing properly. We CCTV'd 4" main and found a 2" piece of plastic hose in main. We called for U.S.A. mark out to make repairs the next day. | N | N | N | None | None | Under the house, percolated into soil | Y | N | N | N/A | 0 | None
040521 | Clay Clifton | 06/09/05 - 4:15 pm | Pat Perkins | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-06-09 13:50 | 2005-06-09 14:30 | 1 | 40 | 40 | 0 | 5010 Avenida Encinas | Carlsbad | 92008 | SD | Sewer Manhole | 0 | N/A | GREASE | Large amount of grease blocking channel | Will CCTV line for condition. Schedule regular routine inspection | N | N | N | None | None | Vactored all sewage | Y | N | N | N/A | 0 | None
040522 | Clay Clifton | 06/14/05 - 14:00 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-06-14 11:10 | 2005-06-14 11:40 | 20 | 600 | 0 | 600 | Hemmingway and Cannon | Carlsbad | 92008 | SD | Manhole on Hemmingway | 0 | N/A | CONSTRUCTION | Blockage in 8" collector main caused overflow. Inspector will have contractor clean and televise the main. | New area, construction just about done. Construction debris most likely the cause | N | Y | N | Strom drain boxes | None | Desilt basin & Storm drain | Y | N | N | N/A | 0 | None
040523 | Clay Clifton | 2005-06-17 | Mark Schilling | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-06-17 08:55 | 2005-06-17 11:30 | 0.5 | 75 | 30 | 45 | Railroad easement Lanikai Ln | Carlsbad | 92008 | SD | 4 inch cleanout | 0 | N/A | DEBRIS | Upturned 45 degree on end of pipe into manhole holds up debris and grease | Line will be put on a bi yearly cleaning schedule | N | Y | N | None | None | Railroad easement where it soaked into soil | Y | N | N | N/A | 0 | Stoppage was not a continuous flow, line was only partially blocked
040524 | Clay Clifton | 06/21/05 - 8:30 | Pedro Rodriguez | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-06-18 15:15 | 2005-06-18 15:35 | 0.5 | 10 | 0 | 10 | Carlsbad Blvd | Carlsbad | 92008 | SD | Campground lift station | 0 | N/A | POWER FAILURE | Sewer pump station power failure. State Beach Campground | Regular maintenance of campground lift station would prevent overflows | N | N | N | None | None | Percolated into the ground - 40 yards from Ocean. Sprayed area with disinfectant | Y | N | N | N/A | 0 | None
040505 | Clay Clifton | 10/18/04 - 13:50 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2005-10-17 16:00 | 2004-10-17 21:00 | 3 | 900 | 900 | 0 | 2515 El Camino Real | Carlsbad | 92008 | SD | Private sewer lateral in mall parking lot | 1 | 2004-08-26 | GREASE | Grease and food debris caused backup in restaurant lateral (private lateral) | Restaurant needs to jet clean the lateral monthly. *City staff routed overflow back into sewer system-no release to environment. | Y | N | N | None | None | Back into Carlsbad sewer system | Y | N | N | N/A | 0 | None | x
040507 | Clay Clifton | 10/29/04 - 12:15 | Don Wasko | 760-438-2722 | Carlsbad Municipal Water District | Carlsbad Municipal Water District | 2004-10-29 12:15 | 2004-10-29 13:00 | 1.5 | 67 | 67 | 0 | 2715 Madison | Carlsbad | 92008 | SD | Property line cleanout | 0 | N/A | ROOTS | Roots growing in sewer lateral cleanout | Televise it, rod it or even repair the pipe. We washed down and recaptured. | Y | N | N | None | None | Vactor the whole spill | Y | N | N | N/A | 0 | None
045001 | Bryan Ott, Voicemail | 2004-07-16 08:00 | Shawn Atherton | 760-753-5018 | City of Encinitas | City of Encinitas | 2004-07-16 01:15 | 2004-07-16 02:25 | 50 | 3500 | 0 | 3500 | 1 San Elijo at Verdi | Encinitas | 92007 | SD | Manhole #B38 | 0 | na | BLOCKAGE | Contractor working for the city was repairing the lift station. Pumping trucks were transferring sewage from wet well to another manhole. Unknowingly, rags from lift station were dumped into manhole, causing the spill. | Sewer line was cleaned using high pressure cleaner. Roots were removed with root cutter. Line was televised and no other problems noted. | N | N | N | None | None | Water percolated into the dirt along railroad tracks | Y | N | N | na | 0 | A complete cleanup of the site was performed. We spread deodorizing crystals into the dirt to remove any possible odors.
045002 | Bryan Ott, Voice Mail | 2004-10-18 10:00 | Paul Hartman | 760-633-2787 | City of Encinitas | City of Encinitas | 2004-10-17 06:00 | 2004-10-17 06:05 | 389 | 1945 | 0 | 1945 | 46 Encinitas Blvd. | Eninitas | 92024 | SD | n/a | 0 | n/a | CONSTRUCTION | Sewer bypass line (not in use at the time) ruptured causing residual sewage in hose to spill into creek | A meeting was held with the contractor and new procedures were adopted. | Y | Y | Y | Cottonwood Creek | Ocean | n/a | Y | Y | Y | 100 yards north and south of entrance of Cottonwood Creek into Moonlight Beach | 3
045003 | Bryan Ott, Voice Mail | 2004-10-29 12:25 | John King | 760-753-5018 | City of Encinitas | City of Encinitas | 2004-10-28 22:30 | 2004-10-28 23:58 | 546 | 43700 | 0 | 43700 | I-5 at Manchester | Cardiff | 92007 | SD | Olivenhain Pump Station | 0 | n/a | PUMP STATION FAILURE | Clogged pump station pump and alarm communication failure | Pump was unclogged and pump station was back online. Alarm system transmitter was replaced with a new one and tested | Y | N | Y | San Elijo Lagoon | Ocean | n/a | Y | N | Y | 1/2 mile north and south of mouth of lagoon | 4 | Information regarding spill and corrective procedures provided by San Elijo JPA personnel. This pump station is maintained and operated by the San Elijo JPA.
045004 | Bryan Ott, Voice Mail | 2004-11-27 16:00 | John King | 760-753-5018 | City of Encinitas | City of Encinitas | 2004-11-27 12:00 | 2004-11-27 12:55 | 10 | 550 | 500 | 50 | Moonlight Beach Snack Bar | Eninitas | 92024 | SD | B-4 | 0 | n/a | OTHER | Sewer line was 90% full of sand, causing partial blockage | 700 feet of sewer line was cleaned, removing all sand from line. This section of sewer line was placed on quarterly trouble spot list. | N | Y | Y | Wier of pipe | n/a | percolated into ground | Y | N | N | n/a | 0
045005 | Bryan Ott, Voice Mail | 2005-04-24 11:50 | John King | 760-753-5018 | City of Encinitas | City of Encinitas | 2005-04-24 08:45 | 2005-04-24 09:35 | 100 | 5000 | 250 | 4750 | 102 Encinitas Blvd. | Encinitas | 92024 | SD | T-17 on Encinitas sewer map Page 11 | 0 | n/a | CONSTRUCTION | Contractor doing work on Encinitas Blvd. Accidentally put rock, asphalt and pieces of clay pipe into sewer line, causing a blockage. | Cleaned sewer line with high pressure jetter truck. Removed two t-gallon buckets of rocks, asphalt and concrete-type debris. | N | Y | Y | Cottonwood Creek | Ocean | Ocean | Y | N | Y | 1500' north and south of entry., every 100' | 5 | Contractor will be invoiced for cost recovery. Contractor will be completing this work by the end of June. Until this date, the sewer line will be inspected daily at the end of each work day for signs of any debris that could cause future blockages.
045008 | Voice Mail | 2004-10-12 10:30 | David Shissler | (949) 497-0328 | City of Laguna Beach | City of Laguna Beach | 2004-02-04 | 2004-10-12 09:30 | 3000 | 3000 | 0 | 3000 | 480 Ocean Avenue | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Construction | The City reconstructed the sewer main in the Downtown area, which included replacing the main on Ocean Avenue. The lateral serving a small video rental store was not reconnected to the new main during construction. Since the owner believed that he was experiencing a blocked lateral, he didn't report the problem until a plumber determined 8 months later that the lateral was not connected to the City's main line. | The lateral serving the business was immediately reconnected after it was confirmed that the lateral was not connected to the new sewer main. | N | N | N | N/A | N/A | Leached into the ground | Y | N | N | N/A | N/A | To determine the approximate discharge volume an attempt was made to use the water bill from the business. According to Laguna Beach County Water District, the meter was turned off or did not record any water during the period of time that the lateral was disconnected. An estimate was based on the reported use by the owner.
045001 | Voice Mail | 2004-07-18 11:45 | Doug Hellman | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2004-06-21 00:01 | 2004-07-18 10:00 | 0.1 | 250 | 240 | 10 | 999 Oriole Drive | Laguna Beach | 92651 | OR | City Main Line | 0 |  | Line Break | Water Quality Staff received a page at 09:20 from Laguna Beach Police Dispatch in reference to a sewer problem at 999 Oriole Drive. Staff arrived on scene at 09:23 and confirmed that the City's main line was plugged and backing up into the residence. | Staff jetted and vacuumed the main line, and noted that the reason for the blockage was due to a partial collapse at the top of the City's main line. Staff removed the broken pieces of pipe, which restored the flow to the collection system, which restored flow to the line at 10:00. | N | N | N | N/A | N/A | Wastewater was removed from the residence by A1 Emergency Services | Y | N | N | N/A | N/A | The City's main line is due for permanent emergency repairs on July 22, 2004. *The start time and overflow rate can only be estimated due to the homeowner being on vacation for the past month. There is also no evidence that the overflow left the residence.
045002 | Brian Kelly | 2004-08-30 15:45 | Bernadette McCusker | (949) 497-0342 | City of Laguna Beach | City of Laguna Beach | 2004-08-30 14:21 | 2004-08-30 14:45 | 75 | 1900 | 1650 | 250 | 647 S. Coast Hwy | Laguna Beach | 92651 | OR | Sewer Lateral Cleanout | 0 |  | Grease | At 14:21 City staff received a call from Public Works Dispatch of a sewer overflow in progress at 647 S. Coast Highway, which was flowing onto Sleepy Hollow Beach. Staff arrived on scene at 14:30 and confirmed that the City's main line was blocked due to grease. | Staff set up at Cleo Street Lift Station and jetted upstream to manhole #E24-020, which restored normal flow to the main line. Meanwhile, Parks Division staff had created a sand berm to contain 1,000 gallons that had overflowed onto the sand from a 900 gallon holding tank. | N | N | N | N/A | N/A | Two yards of sand was removed from the beach and replenished with new sand. The 900 gallons that was in the holding tank was pumped back into the City's sewer system. | Y | N | N | N/A | N/A | The Orange County Health Care Agency notified us that no beach closure was necessary due to the overflow being contained inside the sand berm, the distance from the tide line, the low tide and the fact that the sand surrounding the area was being removed and replenished with fresh sand. Mike Fennessey from the Orange County Health Care Agency arrived on scene during the cleanup process and approved the method of cleanup.
045003 | Brian Kelly | 2004-09-02 16:30 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2004-09-01 20:25 | 2004-09-01 21:20 | 2.7 | 150 | 148 | 2 | 151 Rockledge Terrace | Laguna Beach | 92651 | OR | Manhole #G26-178 | 1 | 2004-04-07 | Roots | Water Quality Staff received a call at 20:25 from Laguna Beach Police Dispatch in regards to sewage coming out of a manhole on Rockledge Terrace. Staff arrived on scene and confirmed that the City's main line was blocked due to roots. | Staff opened the mainline with a high pressure jetter and cleaned from the downstream manhole # G26-191 to manhole # G26-178. | N | Y | N | Storm Drain Box | N/A | The sewage was contained in a private storm drain structure and staff, using a vacuum truck, recovered all sewage. | Y | N | N | N/A | N/A
045005 | Fax | 2004-09-09 17:45 | Bernadette McCusker | (949) 497-0342 | City of Laguna Beach | City of Laguna Beach | 2004-09-04 12:25 | 2004-09-04 13:00 | 0.57 | 20 | 19 | 1 | 664 S. Coast Hwy | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Roots | Staff received a call from Laguna Beach Police Dispatch in regards to a private sewer spill at 664 S. Coast Hwy which had reached the public right of way. We arrived on scene and confirmed that the private lateral had overflowed. | Laguna Beach County Water District switched off the water, which enabled us to break to wash up the sidewalk area and recover all water from the storm drain box. Parks Division employees removed all sand from the box. | N | Y | N | N/A | N/A | The overflow was removed completely from the storm drain box using a vacuum truck. | Y | N | N | N/A | N/A | Courtesy Report - Private Sewer Lateral | x
045004 | Voice Mail | 2004-09-04 20:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2004-09-04 18:10 | 2004-09-04 19:33 | 0.87 | 20 | 0 | 20 | 2817 Rounsevel Terrace | Laguna Beach | 92651 | OR | Sewer Lateral Cleanout | 0 |  | Roots | Staff received notification from Laguna Beach Police Dispatch at 18:50 of a sewer spill in progress at 2817 Rounsevel Terrace. Staff arrived on scene at 19:10 and confirmed that the sewer lateral was running over. Inspection to the City's main line indicated that the main line was plugged due to tree roots, which caused the lateral to run over. | Staff proceeded to clear the blockage using a high pressure jetting machine from the downstream manhole #G27-036 to #G27-008, which restored normal flow to the collection system. | N | N | N | N/A | N/A | The resident had hosed off the area into the grass area at the rear of the property. There was nothing to recover. | Y | N | N | N/A | N/A
045006 | Fax | 2004-10-14 10:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2004-10-13 16:15 | 2004-10-13 16:30 | 1.66 | 25 | 0 | 25 | 385 Mermaid Street | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Debris | At approximately 4:15 p.m. on Wednesday October 13, 204, I received notification from Public Works Dispatch who stated that there was a possible sewer leak at 385 Mermaid Street | Staff responded and arrived on scene at 4:20 pm. and confirmed that the sewer lateral servicing 385 Mermaid Street was plugged and overflowing. Although there was minimal leakage at this time, staff could see that approximately 25 gallons had flowed down Mermaid Street and into a storm drain located at the corner of Glenneyre Street and Forest Avenue. This storm drain leads to the Flood Control Channel that is dammed by sand and retained within the channel adjacent to Main Beach. Nothing in the channel flows to the ocean. | N | Y | N | N/A | N/A | The 25 gallons of sewage was unable to be retrieved from the storm drain and will eventually evaporate and soak into the sand behind Main Beach | Y | N | N | N/A | N/A | Courtesy Report - Private Sewer Lateral | x
045007 | Phone | 2004-11-04 13:15 | Paul Ferrell | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2004-11-04 09:15 | 2004-11-04 09:25 | 16 | 160 | 10 | 150 | 1435 Regatta | Laguna Beach | 92651 | OR | Manhole #G23-073 | 0 |  | Roots | At 9:15 a.m. November 4, 2004 staff received notification from Public Works Dispatch reporting a sewer manhole overflowing at 1435 Regatta Road. Tree roots in the City main line were the cause of the overflow | Using the Aquatech, staff jetted from manhole #G23-098, jetting upstream to manhole #G23-073. This cleared the blockage and restored the flow to the collection system | N | Y | Y | Storm Drain | Open Canyon Area | Storm drain system that feeds into an open canyon area | Y | N | Y | Bluebird Beach | 2 | The sewer overflow entered a storm drain prior to staff arriving on scene and was not recovered. Efforts to recover the spill were not feasible from this storm drain system as the location of the outlet feeds into an open canyon area and travels approximately three-quarters of a mile before reaching the beach. Staff captured wastewater remaining on the street, recovering ten gallons of sewage using sand bags, and washed and recovered water from the affected area.
045009 | Fax | 2005-01-18 16:00 | David Shissler | (949) 497-0328 | City of Laguna Beach | City of Laguna Beach | 2005-01-15 09:00 | 2005-01-15 09:35 | 0.28 | 10 | 9.99 | 0.01 | 264 Legion Street | Laguna Beach | 92651 | OR | Private Lateral | 0 |  | Roots | On Saturday January 15 2005, Wastewater Division Staff John Greybeck and Bob Babcock were notified at 9:36 a.m. by Laguna Beach Police Dispatch who alerted them of a sewer problem at 264 Legion Street. | Staff was on scene when Andrus Plumbing arrived and made repairs to the sewer lateral, which restored flow to the collection system. | N | N | N | N/A | N/A | Approximately 10 gallons vacuumed up into the vactor truck | Y | N | N | N/A | N/A | Courtesy Report - Private Sewer Lateral | x
045010 | Voice Mail | 2005-01-25 10:50 | Paul Ferrell | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-01-25 10:50 | 2005-01-25 10:55 | 20 | 100 | 0 | 100 | 2535 Temple Hills Drive | Laguna Beach | 92651 | OR | Manhole #G20-050 | 0 |  | Roots | On January 25, 2005, I received a call from City of Laguna Beach Police Department at 10:45 a.m. reporting a sewer spill at 2535 Temple Hills Drive. Staff arrived on scene at 10:50a.m we were approached by the resident (James Houtz). He pointed out the manhole running over in his yard. | Staff set up at the downstream manhole G22-043 and jetted to the upstream manhole G22-050 to break the stoppage at 10:55 a.m. this restoring the flow to the collection system. Staff removed 10 pounds of top soil from the flowerbed area and replaced it with new dry soil. | N | N | N | N/A | N/A | Staff could not recover the rest of the spill due to it soaking into the residents yard | Y | N | N | N/A | N/A
045011 | Voice Mail | 2005-02-17 08:40 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-02-16 16:45 | 2005-02-16 17:25 | 0.37 | 15 | 14.99 | 0.1 | 875 Katella | Laguna Beach | 92651 | OR | Private Sewer Lateral | 0 |  | Roots | At 4:45 p.m. February 16, 2005, I was contacted by Laguna Beach Public Works Dispatch advising me of a sewer problem occurring at 875 Katella Street. I arrived on scene at 5:10 p.m. and determined that there was a blockage in the City's mainline, which resulted in the back-up and overflow from a private sewer cleanout located in the rear patio area of 875 Katella Street. | Using a rodding and vacuum truck, staff were able to break the blockage in the sewer mainline at 5:25 p.m., which restored flow to the collection system. The patio was washed and all put back into the collection system. | N | N | N | N/A | N/A | Recovered and put back into the collection system | Y | N | N | N/A | N/A | A televised inspection on the City's main line revealed heavy tree root intrusion from the private sewer lateral, which services 855 Katella Street. This was the source of the blockage into the City's main line and subsequently caused the backup into 875 Katella.
045012 | Voice Mail | 2005-03-01 08:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-02-28 09:00 | 2005-02-28 09:15 | 2.66 | 40 | 0 | 40 | #5 Rockledge | Laguna Beach | 92651 | OR | 6" Mainline | 1 | 2004-09-01 | PRIVATE PROPERTY | On February 28, 2005, I received a phone call at 9:00 a.m. from Annette Henry who resides at # 5 Rockledge Road. Mrs. Henry advised me that when she used water in her home, she observed it overflowing from her property and onto the beach. | Staff cut and removed excess liner from the City main, which restored flow to the collection system. | N | N | Y | Tide Pools | Pacific Ocean | Pacific Ocean | Y | N | Y | N end of Victoria Beach/Rockledge | 4 | Staff proceeded to clear the obstruction from the downstream manhole #G26-189 but encountered an impassible situation fifteen feet from the manhole. Using a closed circuit television inspection (CCTV), it was apparent that the cause of the obstruction in the mainline was the result of a recently lined sewer lateral servicing #5 Rockledge Road. The plumbing company, Roto-Rooter had installed too much liner into the lateral, which resulted in a blockage of the City’s sewer mainline. | x
045013 | Voice Mail | 2005-03-07 17:45 | Paul Ferrell | (949 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-03-07 16:30 | 2005-03-07 17:30 | 0.083 | 5 | 4.99 | 0.01 | 609 Sleepy Hollow Lane | Laguna Beach | 92651 | OR | Private Sewer Pump | N/A |  | Line Break | At 4:30 p.m. on March 7 2005, Water Quality Staff received a call in regards to an illegal discharge occurring from a restaurant at 619 Sleepy Hollow Lane. When staff arrived on scene they noted that the discharge was actually coming from the residential complex at 609 Sleepy Hollow Lane and that the discharge had reached the sand on the beach. Staff located the facility maintenance worker, Candelario Vizcarra (949) 683-2325, who said that the pump had failed due to a broken shaft and while replacing the shaft, sewage had trickled over down the stairs and onto the sand. | All repairs were made by the maintenance worker and the pump is now operating. | N | N | N | Sand at Sleepy Hollow | N/A | Absorbent and disinfectant was used by the maintenance worker to clean up the spill | Y | N | N | N/A | N/A | Courtesy Report - Private Sewer Lateral | x
045001 | Voice Mail | 08/07/04 1910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2004-08-07 14:45 | 2004-08-07 15:45 | 5 | 300 | 300 | 0 | 4406 Kittiwake Street | Oceanside | 92056 | SD | Manhole | 0 |  | DEBRIS | Contractor re-paved the streets and pushed asphault and concrete into the sewer line. | Entry was made to remove debris and contact was made with the offending contractor. | N | Y | N | None | none | Full recovery from Stormdrain. | Y | N | N |  |  | Spill was chased down stream to Old Grove Road and fully recovered.
045002 | Brian | 08/20/04 1530 | Isaac Richardson | 7604355840 | City of Oceanside | City of Oceanside | 2004-08-20 08:35 | 2004-08-20 08:50 | 20 | 300 | 300 | 0 | 3747 Vista Campana South | Oceanside | 920545 | SD | Manhole | 0 |  | ROOTS | Roots blocking main caused overflow. | Cleaned line with rodder and will CCTV line. | N | Y | N | None | none | Full recovery from Stormdrain. | Y | N | N |  |  | City crews cleaned storm drain and recovered 100%.
045003 | Victor | 09/16/04 0807 | Mark Patnode | 7604355840 | City of Oceanside | City of Oceanside | 2004-09-15 16:27 | 2004-09-15 16:38 | 1.5 | 20 | 20 | 0 | 2900 Block of Farel | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots in City line caused overflow. | Line was cleaned by rodder crew. | N | Y | N | None | None | Full recovery from Stormdrain. | Y | N | N |  |  | This 8 inch line was put on root control with Pacific Sewer Maintenance Corp. in Jul04. Line was treated with Vaporooter in Aug04. Line will be TV'd to see if dead roots were cause.
045004 | Victor Vasquez | 09/30/04 0910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2004-09-29 12:55 | 2004-09-29 13:05 | 5 | 200 | 200 | 0 | 3766 Mission Avenue | Oceanside | 92054 | SD | Private Cleanout | 0 |  | PRIVATE PROPERTY | 6-inch private lateral belonging to Shopping Center. | Three vactors on site to recover spill. Code Enforcement called. | N | N | N |  |  | Full recovery from Parking Lot. | Y | N | N |  |  | City handled spill until property management's plumber cleared stoppage around 16… | x
045005 | Victor Vasquez | 09/30/04 0910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2004-09-29 12:55 | 2004-09-29 13:05 | 10 | 400 | 150 | 250 | 1906 Oceanside Blvd. | Oceanside | 92054 | SD | Private Cleanout/Grease Trap | 0 |  | PRIVATE PROPERTY | Small private lateral belonging to Shopping Center. | City damed spill with sand bags until vactor arrived. Called Code Enforcement. | N | Y | Y | Loma Alta Creek |  | Flows pumped out of Loma Alta Slough into La Salina WWTP. | Y | N | N |  |  | Full recovery not possible. Spill contained in Flood Control Channel to Slough, but no public contact. Private plumber cleared stoppage 2130 hours. | x
045006 | Voice Mail | 10/09/04 1525 | Isaac Richardson | 7608010646 | City of Oceanside | City of Oceanside | 2004-10-09 13:30 | 2004-10-09 14:15 | 10 | 450 | 0 | 450 | 3685 Vista Campana North | Oceanside | 92054 | SD | Manhole | 0 |  | LINE BREAK | 8 inch sewer line has a broken and seperated joint. | Flow has been restored and monitored by city on daily basis. Line will be repaired or replaced ASAP. | N | Y | N | None | None | Flow spilled into drain culvert, down to the bottom of a canyon where soaked into the ground. | Y | N | N |  |  | Spill recovery was hampered by location of spill in canyon.
045007 | Voice Mail | 10/20/04 1910 | Mark Patnode | 7604355840 | City of Oceanside | City of Oceanside | 2004-10-20 10:40 | 2004-10-20 10:43 | 200 | 600 | 0 | 600 | Mesa Drive/Garrison | Oceanside | 92054 | SD | Manhole | 1 | 2004-02-28 | INFILTRATION | Heavy,Heavy rains entered system causing overflow due to exceed max. capacity. | Shutting off pumps at Buena Vista lift station relieved system until rain subsided. | Y | Y | Y | Loma Alta Creek | Pacific Ocean |  | Y | N | Y | Mouth of Creek and 200 ft. north and south on beach. | 3 | City designing solution for capacity issue. Staff will be present during future heavy rains at this site.
045008 | Voice Mail | 10/24/04 1345 | Scott Rogers | 7604355840 | City of Oceanside | City of Oceanside | 2004-10-24 07:40 | 2004-10-24 11:20 | 5 | 1100 | 1050 | 50 | 3970 Waring Road | Oceanside | 92054 | SD | Private Lateral | 0 |  | PRIVATE PROPERTY | Unknown substance caused spill. | Quick response to call from OPD, limited spill amount that reached storm drain. | Y | Y | Y | Buena Vista Creek | Pacific Ocean |  | Y | Y | N |  |  | Private spill had large amount due to Prop. Mgr. failure to call plumber. City began recovery ASAP, and stayed until plumber showed. | x
045009 | Victor | 10/25/04 1439 | Jeremy Kemp | 7604355840 | City of Oceanside | City of Oceanside | 2004-10-25 09:48 | 2004-10-25 09:58 | 5 | 50 | 0 | 50 | Valley Glen & Palmer | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots and grease blocked the pipe. | Cleaned Manhole and pipe and dropped 100 lbs. CL2 upstream. | Y | Y | Y | Buena Vista Creek | Pacific Ocean |  | Y | N | N |  |  | Manhole was on course at El Camino Country Club. No possible recovery due to course being saturated by last week's rain. Spill flowed under Vista Way & SR#78.
045010 | Voice Mail | 11/26/04 1540 | Mike Dumas | 7604970137 | City of Oceanside | City of Oceanside | 2004-11-26 12:30 | 2004-11-26 12:36 | 5 | 30 | 30 | 0 | 150 Foussat | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | Grease blockage in City Main caused overflow. | City line was cleaned by City Crew. | N | Y | N | None | None | Overflow was vactored up. | Y | N | N |  |  | City crews cleaned the 8 inch line with a vactor.
045011 | Voice Mail | 12/12/04 1550 | Agung Mertha | 7604355870 | City of Oceanside | City of Oceanside | 2004-12-12 13:30 | 2004-12-12 13:40 | 5 | 50 | 50 | 0 | Mission & El Camino Real | Oceanside | 92054 | SD | Manhole | 0 |  | GREASE | 8 INCH LINE HAD HEAVY GREASE BUILDUP. | Thoroughly cleaned and dropped 100 Lbs. of chlorine upstream. | N | N | N | None | None | Spill pooled in parking lot and was fully recovered. | Y | N | N
045012 | Victor Vasquez | 12/14/04 0843 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2004-12-13 17:15 | 2004-12-13 17:55 | 5 | 200 | 200 | 0 | 3308 Mission Avenue | Oceanside | 92054 | SD | Private Cleanout | 0 |  | UNKNOWN | Private line backed up. Plumber broke stoppage in front of Animal Hospital. | Prop. Mgr. has maint. Sched. With plumber. | N | N | N | None | None | Spill pooled in parking lot and was fully recovered. | Y | N | N |  |  |  | x
045013 | Victor Vasquez | 12/22/04 1533 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2004-12-22 14:15 | 2004-12-22 14:35 | 3 | 60 | 40 | 20 | 950 Seacliff Way | Oceanside | 92054 | SD | Private Manhole | 0 |  | ROOTS | kRoots from a large Date Palm grew into a private manhole blocking the channel. | Notified Property Manager of problem. | N | Y | Y | Loma Alta Creek | None |  | Y | N | N |  |  | Loma Alta Creek is bermed off at the Ocean at this time. No chance of polluting the beach. | x
045014 | Victor Vasquez | 01/03/05 1550 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2005-01-03 10:10 | 2005-01-03 11:10 | 2 | 120 | 0 | 120 | 3907 Waring Road | Oceanside | 92054 | SD | Manhole | 1 | 2004-12-08 | ROOTS | Roots blocked the city's mainline. | Roded out the line. Will inspect with CCTV. | Y | Y | Y | Buena Vista Creek | Buena Vista Lagoon. |  | Y | N | N |  |  | It took Rodder Crew 2.5 hours to break through roots.
045015 | Voice Mail | 01/12/05 1407 | David Sanchez | 7604355842 | City of Oceanside | City of Oceanside | 2005-01-12 10:45 | 01/12/05 1100 | 7 | 105 | 105 | 0 | 300 block North Ditmar | Oceanside | 92054 | SD | Manhole | 0 |  | DEBRIS | Net from Deodorent Block collected rags and debris causing obstruction. | No longer use Deodorant blocks due to past problems. | Y | Y | N |  |  | Full Recovery. | Y | N | N |  |  | Crew vactored up entire spill.
045016 | Victor Vasquez | 02/17/05 1105 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 2005-02-17 07:05 | 02/17/05 0855 | 25 | 2750 | 1875 | 875 | 2302 Valley Glen Drive | Oceanside | 92054 | SD | Manhole | 1 | 2004-10-25 | CONSTRUCTION | Contractor drove his trench plate through side of 10 inch clay sewer main. | Contractor to pay attention to "markouts" and City Inspector. | N | Y | Y | Buena Vista Creek | Buena Vista Lagoon. |  | Y | N | N |  |  | City line is plugged off while contractor bypasses the break, and repairs it.
045001 | Fax | 2004-07-26 15:15 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2004-07-26 11:25 | 2004-07-26 14:00 | 0.05 | 5 | 0 | 5 | Poche Beach in San Clemente | San Clemente | 92672 | OC | Air/Vac Relief | 1 | 2004-06-01 | OTHER | Air/Vacuum relief stuck in the open position | Repaired failed set pin | N | Y | Y |  |  | Pacific Ocean | Y | N | Y | Poche Beach in San Clemente | 3
045002 | Fax | 2004-08-18 14:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2004-08-18 09:01 | 2004-08-18 09:12 | 0.45 | 5 | 0 | 5 | Poche Beach in San Clemente | San Clemente | 92672 | OC | Air/Vac Relief | 2 | 6/1/04 7/26/04 | OTHER | Air/Vacuum relief stuck in the open position | Replaced entire unit again as was done on 6/1/04 | N | Y | Y |  |  | Pacific Ocean | Y | N | Y | Poche Beach in San Clemente | 3
| Fax | 2004-08-23 14:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2004-08-22 23:26 | 2004-08-24 03:00 | 0.6 | 75 | 70 | 5 | 110 North El Camino Real | San Clemente | 92672 | OC | Private grease trap overflow | 0 |  | PUMP STATION FAILURE | Private sewer system failure | Domestic water supply shut off until repairs are complete | N | Y | N |  |  | Returned to Sanitary sewer system | Y | N | N |  |  | Storm drain is diverted into the sewer sysem | x
045005 | Voice Mail | 2004-11-17 17:05 | AJ Howard | 494-366-1553 | City of San Clemente | City of San Clemente | 2004-11-17 13:50 | 2004-11-17 16:15 | 3 | 75 | 75 | 0 | 233 Ave. Granada | San Clemente | 92672 | OC | 8" gravity line | 0 | 0 | OTHER | Diapers | Cleared Obstruction | n | y | n | none | none | Back to sewer system | y | n | n |  |  | Vactor truck recoverd SSO at a lower area of the storm drain system
045006 | Voice Mail | 2004-11-28 18:25 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2004-11-17 15:00 | 2004-11-17 17:05 | 20 | 2400 | 2400 | 0 | 200 Via Turqueza | San Clemente | 92672 | OC | Sewer Manhole | 0 | 0 | ROOTS | Root intrusion into the manhole | Placed on quartely root clearing schedule | n | y | n | none | none | Back to sewer system | y | y | y | Poche Beach | 3 | County Health Officials posted Poche beach as a precaution
045007 | Brian Kelly | 2004-12-20 14:25 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2004-12-20 07:45 | 2004-12-20 08:15 | 20 | 600 | 200 | 400 | 3020 Ave. Del Presidente | San Clemente | 92672 | OC | 8" gravity line | 0 | 0 | VANDALISM | Fence post shoved into manhole | Remove fence post and close manhole | n | n | n |  |  | Dry canyon | y | n | n
| Fax | 2005-01-19 10:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2005-01-19 08:00 | 2005-01-19 08:15 | 1 | 20 | 0 | 20 | 130 Calle Redondel | San Clemente | 92672 | OC | Private Lateral | 2 | 05/07/04 06/01/04 | PRIVATE PROPERTY | Private System | Private Contractor Repair | n | n | n |  |  | Dried into Surround Soil | y | n | n |  |  | Private Sewer | x
045003 | Fax | 2004-10-02 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 10/02/04 11:25hrs | 2004-10-02 11:40 | 1.8 | 8 | 8 | 0 | 3830 Ave Del Presidente | San Clemente | 92672 | OC | 8" gravity line | 0 | 0 | OTHER | Plumber cut roots from private lateral and logged in sewer line |  | n | n | n | none | none | Back to sewer system | y | n | n | n
045004 | Fax | 2004-11-09 15:10 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 11/09/04 11:38hrs | 2004-11-09 13:05 | 1 | 90 | 65 | 25 | 200 Blk of Guadalajara | San Clemente | 92672 | OC | 8" gravity line | 0 | 0 | ROOTS | Root intrusion into the manhole | Root inhibitor injected to the manhole | n | y | n | County flood control channel | Pacific Ocean | Pacific Ocean | y | n | y | Poche Beach | 3
| Fax | 2004-07-27 14:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | Unknown | 7/27/04 11:45am | 50 | 50 | 0 | 50 | 127 N. El Camino Real | San Clemente | 92672 | OC | Private sewer lateral | 0 |  | BLOCKAGE | Private sewer system failure | Domestic water supply shut off until repairs are complete | N | Y | N |  |  | Dry canyon storm drain | Y | N | N |  |  | Private sewer system | x
| Fax | 2004-08-09 14:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | Unknown | 2004-08-06 14:13 |  | 0 | 0 |  | 265 West Marquita | San Clemente | 92672 | OC | Private sewer lateral | 0 |  | LINE BREAK | Private sewer system failure | Domestic water supply shut off until repairs are complete | N | N | N |  |  | Soaked into hillside dirt | Y | N | N |  |  | Private sewer system quanities of spill are Unknown | x
| Fax | 2005-03-15 15:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | Unknown | 2005-03-15 09:00 |  | 300 | 60 | 240 | 265 W. Marquita | San Clemente | 92672 | OC | Private Lateral | 1 | 2004-08-06 | PRIVATE PROPERTY | Private System | Private Contractor Repair | n | n | n |  |  | Dried into Surround Soil | y | n | n |  |  | Private Sewer | x
045001 | Victor Vasquez, (858)571-6972 | 2004-09-16 16:30 | Greg Marquard | (949) 443-6367 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-09-11 09:55 | 2004-09-11 10:30 | 1 | 35 | 0 | 35 | 32012 Calle Delgado | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | GREASE | Grease was built up in main sewer line | Jetted mainline thoroughly; cctv videotaping of mainline; area put on priority maintenance schedule | N | Y | N | none | none | storm drain | Y | Y | N
045003 | Quarterly Report | Quarterly Report | Phil Falzarano | (949) 443-6396 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-10-19 08:30 | 2004-10-19 10:00 | 8.8 | 792 | 0 | 792 | Via Cristal | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | CONSTRUCTION | Rocks and debris in mainline blocking flow, which appears to be due to construction debris. | Jetted mainline before and after blockage; cctv videotaping of mainline; | Y | Y | Y | San Juan Creek | Pacific Ocean | San Juan Creek | N | N | N
045002 | FAX 858-571-6972 | 2004-12-08 10:00 | Michelle Perea | (949) 487-4315 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-12-07 15:55 | 2004-12-07 16:28 | 50 | 1600 | 0 | 1600 | Intersection of Ortega Hwy/Belford Dr | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | ROOTS | Roots in sewer line caused grease to build up, which in turn, caused the overflow. | City Contractor removed obstruction of roots and jetted the line several times. Sewer line will be cleaned in Feb/March 2005. | Y | Y | Y | San Juan Creek | Pacific Ocean | Pacific Ocean | Y | Y | N
045019 | faxed | 2004-09-02 08:32 | George Solano | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2004-09-02 08:32 | 2004-09-02 09:44 | 2 | 144 | 144 | 0 | 2112 E. Vista Way | Vista | 92084 | SD | PRIVATE LATERAL | 0 | N/A | Private Property | Improper maintenance of private lateral | Turned over to City of Vista Stormwater Pollution Prevention Office for corrective action. | N | N | N | None | None | Vactor truck | Y | N/A | N | N/A | N/A | Private Sewer System | x
045020 | faxed | 2004-10-12 15:30 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2004-10-12 08:24 | 2004-10-12 08:37 | 1 | 15 | 15 | 0 | 305 Bobier Drive | Vista | 92083 | SD | V11 | 0 | N/A | Roots | Roots from a private lateral grew into city mainline causing blockage | City crews root cut line and treated line with RootX. City will notify citizen of improperly maintained 4" lateral. | N | Y | N | None | None | Storm drain box vacuumed by city crews. | Y | N/A | N | Around broken 8" pipe | 2 | Signs will be removed on 10/14/04 when area has dried out. Area is blocked off.
045021 | faxed | 2004-10-27 07:20 | David Brookbank | 760.726-1340 | City of Vista | City of Vista | 2004-10-27 19:15 | 2004-10-27 19:35 | 5 | 100 | 0 | 100 | 330 S. Santa Fe Avenue | Vista | 92083 | SD | V24 | 0 | N/A | Roots | Roots in line; will televise line to find cause | City crews cleaned with sanitary cleaning head on vactor; recleaned with chain flail and televised. Unable to reclaim water due to rainfall. | Y | Y | Y | Buena Vista Creek | None | Diluted into storm drain by rain | Y | N/A | N | N/A | N/A | No public access to storm drain
045024 | faxed | 2005-01-10 15:40 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-01-09 11:00 | 2005-01-09 02:00 | 25 | 21000 | 21000 | 0 | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 0 | N/A | Flood damage | Infiltration due to heavy rain showers from heavy rain storm that hit the area | Raceway pump station will be soon replaced with a new pump station. The City of Vista sent out the bids for the new pump station. The bid opening for the pump station is March 25, 2005. | Y | N | N | None | None | Retention area around station compound | Y | N/A | N | Perimeter of compound | Still posted | Raceway pump station is still under guarded condition with crews stationed at pump station 24-hours until storm passes. Also have pumper trucks running around the clock until storm passes.
045026 | faxed | 2005-01-12 10:05 | Jim Gusman | 760.726-1340 | City of Vista | City of Vista | 2005-01-11 08:00 | 2005-01-11 08:10 | 100 | 2300 | 2300 | 0 | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 0 | N/A | Flood damage | Heavy rain | Work with Encina Wastewater Authority to bypass and ramp down Buena Pump Station to allow Vista to continue pumping into shared pressure main. Also brought in up to four pumper trucks to transfer flow to the Vista/Carlsbad interceptor trunk line | Y | N | N | None | None | Raceway Pump Station holding/containment area | Y | N | N | Around pump station and containment area | Still posted | Wash down area with bleach today (01/12/05) capture and pump out containment area. OEM not notified because spill contained to pump station area.
045025 | faxed | 2005-01-12 07:45 | Richard Flynn | 760.726-1340 | City of Vista | City of Vista | 2005-01-11 15:16 | 2005-01-11 16:04 | 25 | 1200 | 700 | 500 | 455 Hillway Drive | Vista | 92083 | SD | V23 | 0 | N/A | Roots | Excessive amount of storm water and roots caused gravity flow sewer line to become blocked resulting in overflow and spill. | Preventive maintenance, CCTV survey and infiltration preventive practices and BMPs. | Y | Y | Y | Beaumont Easement Storm Channel | Buena Vista Creek |  | Y | N/A | N | Beaumont School | Still posted | Due to heavy ground water saturation and heavy rain showers could not effectively capture 100%. Amount of stormwater flow was at flood stage at the time of spill, estimated flow of stormwater was at 50 GPM.
045027 | faxed | 2005-02-21 19:29 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-02-21 10:20 | 2005-02-22 10:30 | 5 | Unknown | 200 | Unknown | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 2 | 2005-01-11 | Infiltration | Heavy, record breaking rain in county; inflow and infiltration | The new Raceway Pump Station will soon be built. Scheduled completion date is December 2005. | Y | N | Y | Aqua Hedionda Creek | None | Creek | Y | N | N | None - to dangerous to post at this time | N/A | Heavy rains filled our holding area causing some of the contamination runoff and sewage to hit the creek.
045028 | faxed | 2005-02-22 19:29 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-02-22 07:37 | 2005-02-22 07:42 | 5 | 25 | 25 | None | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 2 | 1/11/2005, 2/21/2005 | Infiltration | Heavy, record breaking rain in county; inflow and infiltration | City of Vista was at the pump station during one of the heavy rain events causing a small amount of sewage left the wet well. Crews adjusted accordingly and vacuumed up the spill. | Y | N | N | Holding area around pump station | None | Holding area around pump station | Y | N | N | None | N/A | Heavy rains came through our area causing small spill, approximately 25 gallons.
045030 | faxed | 2005-03-26 09:30 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2005-03-26 06:00 | 2005-03-26 07:40 | 10 | 60 | 45 | 5 | 1244 N. Santa Fe Avenue | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | Contacted property management, no response. Followed up by calling ASAP Plumbing to clear drain along with Vista Irrigation District (Mark) to shut off water at complex to stop overflow. Overflow area was damned off (06:40) Vactor truck (Unit 527) was used to vacuum up overflow and washed down. | Y | Y | N | None | None | Storm drain at N. Santa Fe Avenue and W. Indian Rock Road | N | N | N | N/A | N/A | Plumber on scene at 07:25, Vista Irrigation District on scene at 07:40, water turned off at 07:50. | x
045032 | faxed | 2005-03-26 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2005-03-26 14:05 | 2005-03-26 17:00 | 3 | 540 | 500 | 40 | 1205 Monique Court, Units A - D | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | Called out ASAP Plumbing Co. to clear blockage. Damned up flow and used Vactor #527 to vacuum up water and washed down area. Line cleared at 17:00. Resident advised to stop water usage at 16:30. | Y | N | N | None | None | Private property in house. | N | N | N | N/A | N/A | Was told by resident that this has been an on-going problem for approximately four (4) days; unable to determine exact duration at this time. | x
045031 | faxed | 2005-03-27 16:51 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE LATERAL | 2005-03-27 11:54 | 2005-03-27 14:00 | 10 | 850 | 0 | None | 1333 Olive Avenue (Tiki Village Mobile Home Park) | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | All but 10 gallons were contained in space #26 bathrooms (2) and interior of house some sewer was under house and we were able to contain this small amount by damning it. Property owner had ASAP Plumbing Co. clear the line at 14:00 hrs. Gave property owner and manager copy of the City of Vista policy explaining owner responsibility. | Y | N | N | None | None | Private property in house. | N | N | N | N/A | N/A | All sewage was contained at space #26. Property owner was made aware of damage to space #26. | x
045023 | faxed | 2004-12-17 08:30 | George Solano | 760.726-1340 | City of Vista | PRIVATE LATERAL | Unknown | 2004-12-17 16:00 | Unknown | Unknown | 1000 | Unknown | 993 Postal Way | Vista | 92083 | SD | PRIVATE LATERAL | 0 | N/A | Roots | Improper maintenance of private 8" VCP sewer system | Storm Water compliance officer, Sandi Sotola will be following up on this call. | N | Y | N | None | None | Storm drain (very hot day 80 degrees +) | Y | N/A | N | N/A | 0 | Private Sewer System | x
045029 | faxed | 2005-03-11 09:40 | Jim Gusman | 760.726-1340 | City of Vista | PRIVATE SEPTIC SYSTEM | Unknown | 2005-03-11 | 1 | Unknown | 100 | Unknown | 1138 Cielita Linda | Vista | 92083 | SD | Private septic sewer system | N/A | N/A | Unknown | Unknown | Vacuumed and washed down right-of-way, sandbagged and bermed spill area and catch basin; notified storm drain enforcement officer. Sample tested, high fecal count, dye tested on 03/10/2005, no results as yet. Either from 1134 or 1138 Cielita Linda. | Unknown - none during response notification or on 03/09/2005 | Unknown | Unknown | None | None | N/A | Y | N | Y | 1138 Cielita Linda | N/A | Turned over to Mikhail Ogawa - 619.994.7074 | x
045001 | Clay Clifton | 2/22/2005 1530 pm | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 02/21/05 1330 | 02/21/05 1345 | 5 | 100 | 0 | 100 | 5682 Sweetwater Rd | Bonita | 91978 | SD | 590-052-190H | 0 | NA | Infiltration | Heavy rainfall | Check for infiltration upstream | Y | N | Y | Sweetwater River | NONE | NA | Y | N | N | NO | 0
045001 | Victor Vasquez (858) 636-3155 | 2004-07-29 10:50 | Renzo Marin | (949) 837-7050 | El Toro Water District | El Toro Water District | 2004-07-29 09:15 | 2004-07-29 09:45 | 2 | 60 | 0 | 60 | 712 Avenida Majorca | Laguna Woods | 92654 | OC | ETWD Atlas page ME- 495 | 0 | N-A | ROOTS | Roots blockage in 8" sewer line. | Used Jetter to break blockage. TV inspection revealed roots in the pipeline. The line was root cut the next day, July 30,04. Will TV line 8/4/04 to assess line conditions with a follow up inspection in six (6) months. | N | Y | Y | Catch basin | Aliso Creek | Aliso Creek | Y | N | N | N-A |  | Notified Regulatory agencies. Emailed report to all agencies and City of Laguna Woods. This line was last cleaned January 2003.
045002 | Victor Vasquez (858) 636-3155 | 2004-10-14 18:20 | Dennis Cafferty | (949) 837-7050 | El Toro Water District | El Toro Water District | 2004-10-14 16:45 | 2004-10-14 18:00 | 125 | 9625 | 250 | 9375 | Moulton Pkwy & Via Inglesia | Laguna Woods | 92654 | OC | ETWD Atlas page MD- 494 | 0 | N-A | ROOTS | Tree roots obstruction in sewer manhole. | Used Jetter to break blockage. Removed all roots from manhole. TV inspection and further Jetting conducted on 10/15/04 to verify removal of all roots. Will a follow up inspection in six (6) months. | N | Y | Y | Storm drain | Aliso Creek | Ocean | Y | Y | Y | Aliso Beach | 3 | Applicable Cities and Regulatory Agencies notified by phone 10/14/04. Emailed Report 10/15/04. Line was last TV inspected 12/02 and cleaned in 01/03.
045003 | Delia (858) 639-3155 | 2005-02-19 13:00 | Troy Davis | (949) 837-1660 | El Toro Water District | El Toro Water District | 2005-02-19 10:00 | 2005-02-19 10:15 | 50 | 750 | 0 | 750 | 25011 El Toro Road, LW ETWD OSO Lift Station | Laguna Woods | 92654 | OC | ETWD Atlas page ME-485 | 0 | N-A | Power failure | Pump # 1 unable to pump at full capacity do to the discharge check valve failing to completelly open. Cleared obstruction in check valve by pulling check valve arm open. Repeated action several times untill obstruction passed through the valve and put pump back in operation. | At the time the failure occured the Station was unable to handle the peak flow with one pump and the overflow occured at manhole inside station. | Y | Y | Y | Storm drain | Laguna Canyon Channel | Laguna Main Beach | Y | Y | Y | Laguna Main Beach | 3 | Applicable Cities and Regulatory Agencies Notified 2/19/05. Emailed Report 2/24/05.
045001 | FAX | 7/11/04 1300 | John Fox | (949) 494-8571 | Emerald Bay Community Services District | Emerald Bay Community Services District | 7/11/04 0530 | 7/11/04 0605 | 10 | 350 | 100 | 250 | 241 Emerald Bay | Laguna Beach | 92651 | OC | Pump Station #4 | 0 |  | DEBRIS | Float failure occurred causing pumps to airlock. Debris (not found) probably prevented floats from closing. Nature of debris unknown but possibly from construction. | Continue frequent wet well cleaning. Last cleaning prior to this incident was June 29, 2004. Plan a reminder to every construction supervisor about the importance of protecting EBSD facilities. | N | Y | N | Storm drain catch basins | Upper beach sand | Upper beach sand | Y |  | Y | Upper storm channel at beach | 5 | Following return of pump station to operation, storm channel was thoroughly washed into catch basins for immediate return of contamination to sewer system.
045012 | FAX (858) 571-6972 | 1/11/2005 13:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 1/11/2005 07:30 | 2005-01-11 08:00 | 15 | 450 | 100 | 350 | 2857 S. Mission Rd. - Overland PS | Fallbrook | 92028- | SD | Pump Station | 0 |  | POWER FAILURE | Pump station had a power failure. | Restored power at pump station. | Y | N | Y | Ostrich Creek | San Luis Rey, Pacific Ocean |  | Y | N | Y | Along creek | 3 | Very high flow at pump station during power failure.
045013 | FAX (858) 571-6972 | 1/11/2005 13:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Private Party | 1/11/2005 11:14 | 1/11/2005 11:20 | 1 | 6 | 0 | 6 | 655 E. Alvarado | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Paper products blockage. | Rodded lateral and opened at about 7 feet. | Y | N | Y | Fallbrook Creek | Lake O'Neill, Santa Margarita River, Pacific Ocean | ** Along side of road, but had considerable rainfall runoff as well, which may have caused it to reach surface waters. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Sewage was standing in cleaout and barely trickling out of box. Overflow went along side of road, but listed surface waters due to considerable rainfall runoff still flowing along side of road. | x
045014 | FAX (858) 571-6972 | 1/23/2005 20:00 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 1/23/2005 08:00 | 1/23/2005 10:00 | 30 | 3600 | 100 | 3500 | 2800 Block Overland Trail | Fallbrook | 92028- | SD | Force Main | 2 | 12/28/04, 01/09/05 | LINE BREAK | Force main line broke. | Removed approximately 20 feet of pvc pipe and sectioned in new C-900. | N | N | Y | Ostrich Creek | San Luis Rey River, Pacific Ocean |  | Y | Y | Y | Along Ostrich Creek | 3 | Removed contaminated soil.
045011 | FAX (858) 571-6972 | 1/8/2005 01:45 | Eddie Taylor | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 1/7/2005 23:00 | 1/8/2005 01:30 | 12 | 1830 | 0 | 1830 | 800 block Palomino Road | Fallbrook | 92028- | SD | Manhole | 1 | 9/04/04 | UNKNOWN | Manhole overflowing in middle of a spill way. Extreme rainfall and flow caused manhole lid to rise, resulting in overflow. | Flushed main line to relieve blockage. Will place locking manhole lid at this location. | Y | N | Y | Un-named creek along Palomino Road | Ostrich Creek, San Luis Rey River, Pacific Ocean |  | Y | Y | N |  | 0 | Have no idea how long it had been running due to rain, had to estimate.
045010 | FAX (858) 571-6972 | 1/9/2004 21:00 | Eddie Taylor | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 1/9/2005 20:00 | 1/9/2005 20:45 | 42 | 1875 | 0 | 1875 | 2800 block S. Mission Road | Fallbrook | 92028- | SD | Manhole | 1 | 12/28/04 | DEBRIS | Broken pipe (debris) in manhole. High flows from rainfall contributed to pipe break and overflow. | Flush mainline to relieve blockage. | Y | N | Y | Ostrich Creek | San Luis Rey River, Pacific Ocean |  | Y | Y | Y | Along the creek | 3 | Found PVC pipe blocking main line.
045004 | FAX (858) 571-6972 | 10/6/2004 11:30 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/6/2004 06:58 | 10/6/2004 07:25 | 75 | 2025 | 0 | 2025 | 200 Block of Hawthorn Street | Fallbrook | 92028- | SD | Manhole | 1 | 05-02-04 | VANDALISM | Flushed mainline and pulled back two plastic bottles and coke cans. Grease in mainline also. | Flushed mainline several times, vacuumed out strom drain inlet. | N | Y | Y | Fallbrook Creek | Lake O'Neill, Santa Margarita River, Pacific Ocean | NA | Y | Y | N |  | 0 | Manhole located next to storm drain inlet. Removed storm drain cover and washed down and vacuumed box. Don't know exact storm drain flow route, but believe it flows into Fallbrook Creek about 1/4 mile away.
045005 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 10/6/2004 08:15 | 10/6/2004 08:45 | 5 | 150 | 100 | 50 | 104 W. Elder Street | Fallbrook | 92028- | SD | Manhole | 1 | 10-06-04 | ROOTS | Roots in manhole causing blockage. | Vacuumed out manhole. Removed roots and flushed mainline. Put Root-Z in manhole. | N | N | N |  |  | Ran down asphalt parking lot into dirt alleyway and onto asphalt street puddling up in low spot. Vactored up puddle and disinfected area. | Y | N | N |  | 0 | Vacuumed wet dirt in alley, standing water on asphalt, and washed down asphalt. Disinfected area and vacuumed.
045006 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/15/2004 08:45 | 12/15/2004 09:30 | 1 | 45 | 35 | 10 | 825 Winterhaven | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Rags and paper towels in lateral. | Rodded cleanout and flushed main line. Washed down asphalt parking lot and vacuumed up wash down water. | N | N | N | None | None | Parking lot of bus barn. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Vacuumed wash down water and disinfected. | x
045007 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/22/2004 13:00 | 12/22/2004 13:30 | 1 | 30 | 25 | 5 | 861 E. Alvarado | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Paper products. | Unstopped private line. Washed down and vactored up. Disinfected recovered wash down. | N | N | N |  |  | Around cleanout. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Washed down and vactored up overflow and disinfected area. | x
045008 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/26/2004 14:00 | 12/26/2004 14:30 | 1 | 30 | 25 | 5 | 861 E. Alvarado | Fallbrook | 92028- | SD | Cleanout | 1 | 12/22/04 | PRIVATE PROPERTY | Paper products. | Ran rodder 80' and cleared stoppage. Put bullet on and ran again. Washed down and vactored up disinfected area. | N | N | N |  |  | Around cleanout. | Y | N | N |  | 0 | COURTESY NOTIFICATION. Washed down and vactored up overflow. Disinfected area. | x
045009 | FAX (858) 571-6972 | 1/4/2005 08:45 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 12/28/2004 08:45 | 12/28/2004 09:15 | 100 | 3000 | 0 | 3000 | 2800 S. Mission road | Fallbrook | 92028- | SD | Force Main | 0 |  | LINE BREAK | Force Main | Repaired and installed new pipe. | Y | N | Y | Ostrich Creek | San Luis Rey River, Pacific Ocean |  | Y | Y | Y | Along Ostrich Creek | 3 | Repaired force main. Overflow volume is based on duration of pump cycle and gpm (estimated for report as "maximum possible").
045015 | FAX 858-571-6972 | 2/10/2005 14:10 | Patti S. Page | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 2/10/2005 06:55 | 2/10/2005 07:05 | 1.5 | 15 | 10 | 5 | 500 Block E. Alvarado x Brandon Street | Fallbrook | 92028- | SD | Manhole | 0 |  | GREASE | Grease in mainline. | Flushed mainline on 500 Block E. Alvarado and Brandon Street. Washed down area and vacuumed up wash down water. | N | Y | N | None. | None. | Dammed up gutter to stop flow into drain. | Y | N | N |  | 0
045017 | FAX (858) 571-6972 | 3/18/2005 07:30 | Jeff Parks | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utility District | 3/17/2005 10:45 | 3/17/2005 11:00 | 2 | 30 | 30 | 0 | 990 E. Mission Road | Fallbrook | 92028- | SD | 4" Cleanout | 0 | NA | PRIVATE PROPERTY | Roots about 90 feet into lateral from cleanout. | Rodded open and veiwed with lateral camera. Washed down parking lot and disinfected. | N | N | N | None. | None. | Parking lot to office. | Y | N | N |  | 0 | Dammed up flow before it reached storm drain. Vacuumed up all overflow and wash down water. Will apply Root-X to lateral in six weeks. | x
045018 | VOICEMAIL (858) 467-2952 | 3/19/2005 19:30 | Kyle Drake | (760) 728-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 3/19/2005 11:00 | 3/19/2005 12:00 | 35 | 2100 | 0 | 2100 | 2800 Block Overland Trail | Fallbrook | 92028- | SD | Force Main | 3 | 12/28/04, 01/09/05, & 1/23/05 | LINE BREAK | Five foot section of pipe split at the bottom. | Removed bad section of pipe and replaced with new. | Y | N | Y | Ostrich Creek | San Luis Rey River, Pacific Ocean |  | Y | Y | Y | Along Ostrich Creek | 3 | Due to weekend reporting, County HM should have notified OES.
045019 | FAX (858) 571-6972 | 3/30/2005 13:55 | Patti S. Page | (760) 128-1125 | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 3/30/2005 11:00 | 3/30/2005 11:45 | 20 | 900 | 30 | 870 | 721 Shady Lane | Fallbrook | 92028- | SD | 4" Cleanout | 0 |  | GREASE | Grease blockage in mainline. | Flushed and opened with vactor. Ran mainline a second time. Washed down road and vacuumed up puddles in dirt. | Y | N | N | None. | None. | Across road and into dirt field. | Y | N | N |  | 0
045016 | FAX (858) 571-6972 | 3/4/2005 20:00 | Devin Casteel | (760) 728-1125 | Fallbrook Public Utilities District | Private Party | 3/4/2005 16:30 | 3/4/2005 17:30 | 1 | 60 | 5 | 55 | 410 East Fallbrook Street | Fallbrook | 92028- | SD | Cleanout | 0 | 0 | PRIVATE PROPERTY | 6" cleanout plugged with paper products around 15 feet from cleanout. | Ran rodder with 6" cutter to clear stoppage | Y | Y | Y | Fallbrook Creek | Lake O'Neill |  | Y | N | Y | Along Fallbrook Creek | 3 | After spill was cleared. Scraped up waste and filled one 5-gallon bucket. Used 50 gallons of wash down after and recovered all. Sprayed disinfectant around area. And vactored out 150 gallons at creek. | x
045001 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 8/30/2004 10:50 | 8/30/2004 11:00 | 1 | 10 | 5 | 5 | 224 O'Hearn Drive | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Roots from nearby trees. | Rodded lateral, and root-x'd line. | N | N | N | None | None | Soaked into ground around cleanout box. | N | N | N |  | 0 | PRIVATE SEWER - COURTESY NOTIFICATION. | x
045003 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 9/30/2004 08:36 | 9/30/2004 11:30 | 0.5 | 91 | 0 | 91 | 400 W. Fallbrook Street | Fallbrook | 92028- | SD | Cleanout | 0 | NA | PRIVATE PROPERTY | Blockage occurred from past construction. | Located cleanout and removed blockage. Also flushed main line and TV'd main line. | N | N | N |  |  | Around cleanout and soaked into the ground. | Y | N | Y | Around contaminated area. | 3 | COURTESY NOTIFICATION. School District is going to remove the soil that was affected. | x
045002 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 9/4/2004 11:30 | 9/4/2004 12:05 | 3 | 105 | 0 | 105 | 820 Cookie Lane | Fallbrook | 92028- | SD | Cleanout | 0 | NA | ROOTS | Roots in mainline. | Flushed mainline, found blockage at 36 feet. | N | N | N | None | None | Along side of road in field. | Y | N | N |  | 0 | Disinfected along the roadway where it traveled into field.
045001 | FAX (858) 571-6972 | 2005-01-11 08:00 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2005-01-10 14:30 | 2005-01-10 15:48 | 150 | 12000 | 6000 | 6000 | Clubhouse & Niguel Rd. | Laguna Niguel | 92677 | OR | 8" Forcemain from Upper Salada Lift Station | 0 | 0 | Line break | Line failure - 2" hole in ductile iron pipe | Repair clamp installed as emergency measure. New section of pipe installed within 7 days. | Y | Y | Y | Salt Creek | Pacific Ocean |  | Y | Y | Y | Salt Creek Beach
045002 | FAX (858) 571-6972 | 2005-01-14 16:30 | Larry Dees | (949) 425-3537 | Moulton Niguel Water District | Moulton Niguel Water District | 2005-01-14 11:30 | 2005-01-14 11:40 | 4 | 40 | 20 | 20 | Dolphin Cove | Laguna Niguel | 92677 | OR | Manhole | 0 | 0 | Blockage | Paving contractor poured excess asphalt into manhole causing a blockage. | Jackhammered and removed asphalt. Sent letters to local paving contractors stating the importance of maintaining clean sewers and the consequences of causing blockages, and that the District will remove debris dropped into sewer by contractor at no cost if contractor notifies District. | Y | Y | Y | Sulphur Creek Reservoir |  | VacCon truck | Y | N | N |  |  | Sewer serves six homes
045003 | FAX (858) 571-6972 | 2005-03-31 08:00 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2005-03-30 18:30 | 2005-03-30 19:25 | 15 | 825 | 225 | 600 | Aliso Creek/Autumn Glen | Aliso Viejo | 92656 | OR | Manhole #23 Sect. Page D-14 | 0 | 0 | Blockage | Found an 8" piece of PVC pipe material in the 8" sewer line causing partial flow restriction and sewer backup. | Construction debris removed. Video inspected upstream sewers for over 1,000 feet. No problems or other obstructions found. Sewer in great shape. | N | Y | Y | Aliso Creek | Aliso Creek Beach |  | Y | N | N |  |  | Not sure of beach closure.
034009 | Voice message | 2004-07-22 03:10 | Ramon G. Zuniga | (760) 728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2004-07-22 13:29 | 2004-07-22 14:06 | 0 | 0 | 0 | 0 | 31110 Old River Road | Bonsall California | 92003 | SD | Sewage Manhole | 0 | N/A | Blockage | Manhole lid sweating on arrival unblocked blockage with Rainbow Municipal Water District Combination truck followed by C.C.T.V came across sewage v.c.p pipe break and roots, unknown metal object inside 8" v.c.p. pipe north of M/H #. 29F-M010 OlD River Road | Collections crew responded to possible sewage spill at Old River Road in Bonsall unknown address. Sanitation crew immediately began searching for spill came across manhole sweating at 31110 Old River Road . Crew removed manhole lid open and vaccumed manhole to avoid sewage spill. Crew high psi cleaned 310' of sewer lines from M/H 29F-MO15-29F-M010 . Followed by recovering 2 (5 gallons) of soiled ground removed and contained inside combination vehicle for proper dispossal. Rainbow Municipal Water District contracted (Orion Construction Company) phone #. 1-760-591-9181 to excavate and make neccesary pipe repairs on 07-27-2004 pending utulity mark outs before excavation) Under Ground Service Alert Ticket #. 2051163 phone # 1-800-227-2600. | N | N | N | N/A | N/A | Sewage overflow percolated unto manhole exterior barrel and minimal impact on ground | Y | N | Y | Around Manhole | 4 | Sewage spill call came in at 1:29 p.m. on 07-22-2004 forwarded to collections Department in which crew was immediately dispatched to check on spill.
045001 | Victor Vasquez | 2005-01-09 22:00 | Ramon Zuniga | 760-728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2005-01-09 21:40 | 2005-01-09 22:45 | 25 | 1625 | 100 | 1525 | 5708 North River Rad | Ocean side | 92057 | SD | Collection System manhole | 0 | 0 | FLOOD DAMAGE | Heavy rain caused inflow and infiltration to overflow collection system caused 65 minute sewage spill. | City of Oceanside Public Works Department found sanitary sewer spill and called Rainbow Municipal Water District to respond. Staff located sewer manhole gurgling and took immediate action by setting up sand bags at mouth of storm drain. District used its own forces, used Districts combination unit to unblock surcharged line. Disinfected area after removal of debris. Staff will continue to clean and flush out and vactor out collection system on 01-10-2005 to avoid further problems. | Y | Y | Y | San Luis Rey River | Pacific Ocean | Sewage was released on roadway and routed unto storm channel into San Luis Rey River | Y | N | Y | City of Oceanside beach Lifeguard to post | 0 | Per : Environmental Health Services Clay Clifton request to drop of wooden stakes and warning signs to City of Oceanside Lifeguard tower.Gave materials to Lieutennat Kerns, to place around beach access.
| Victor Vasquez | 2005-03-06 19:50 | Brian Fonseca | 760-728-1178 | Rainbow Municipal Water District | Rainbow Municipal Water District | 2005-03-06 17:50 | 2005-03-06 18:30 | 0 | 50 | 0 | 50 | 31940 Del Cielo Oeste | Bonsall | 92003 | SD | Private 3'' sewer clean out - Unit # A,B,C | 0 | 0 | BLOCKAGE | Upon arrival of location techician noticed heavy toilet paper and debris on asphalt driveway. | Technician immediately advised public to keep away from sewage spill area and began to disenfect area by applying RDX44 solution to sterilize area, and then swept up scattered debris and dispossed of properly in plastic containers to dispose of properly at District headquarters . Landlord tennant called Roto- Rooter to assist on clearing blockage at private 3'' sewage latteral. Advised tenant/ landlord to keep annual maintennace on sewer latterals and keep cleanouts cleaned and accessible for unknown emergencies. | N | N | N | N/A | N/A | Tennat asphalt driveway lot to condos | Y | N | N | Placed cones around cleanout (1 day) | 0 | Customer called Roto-Rooter to take care of 3'' surcharged sewer lines and advised plumber to dispose of sewage debri properly and redisenfect area before he leaves area. | x
045001 | FAX (858) 571-6972 | 2004-09-07 09:35 | Steve Francis | (949) 459-6539 | Santa Margarita Water District | Santa Margarita Water District | 2004-09-07 09:15 | 2004-09-07 09:30 | 20 | 300 | 100 | 200 | Devens Way | Ladera Ranch | 92688 | OC | Manhole | 0 | 0 | OTHER | Bulkhead was not removed from system prior to occupancy. | Contained the spill. Vactored the manhole to remove the bulkhead and disinfected the containment area. | N | Y | Y | Ladera Retention Basin | None | N/A | Y | Y | N | N/A | 0 | OES #04-4636
045002 | FAX (858) 571-6972 | 2004-10-20 09:30 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2004-10-20 08:17 | 2004-10-20 08:30 | 50 | 650 | 200 | 450 | 24152 Antonio Pkwy | Rcho Santa Margarita | 92688 | OC | Manhole | 0 | 0 | OTHER | Very heavy rainfall flooded streets and allowed water to enter sewer through pickholes in the manhole covers | Crews started emergency pump and brought down wet well level | Y | Y | Y | Trabuco Creek | San Juan Creek | Pacific Ocean | Y | Y | N | N/A | 0 | OES #04-5452
045003 | FAX (858) 571-6972 | 2004-11-04 08:00 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2004-11-03 21:15 | 2004-11-03 23:20 | 5 | 625 | 125 | 500 | Tossamar/Jardines | Mission Viejo | 92690 | OC | Manhole | 0 | 0 | ROOTS | Blockage in main line. Belileved to be a root ball cut from a customer's lateral. Line was cleaned in August 2004. | Used Vactor to remove blockage. Crew recovered about 125 gallons. | N | Y | Y | Trabuco Creek | San Juan Creek | Pacific Ocean | Y | Y | N | N/A | 0 | OES #04-5742
045004 | FAX (858) 571-6972 | 2004-11-16 13:45 | Gerre Bedell | (949) 459-6541 | Santa Margarita Water District | Santa Margarita Water District | 2004-11-16 11:45 | 2004-11-16 12:30 | 10 | 450 | 0 | 450 | Corportate Drive/Terrace Drive | Ladera Ranch | 92688 | OC | Manhole | 0 | 0 | DEBRIS | Caused by a buildup of rags due to low flow conditions coming from a new, but not fully developed area. | Will be added to the trouble spot list and cleaned every four-months until the area is fully developed. | N | Y | Y | Wet land basin | Holding Basin | Retention Basin | Y | Y | N | N/A | 0
045006 | Voice & Fax | 2005-01-12 10:45 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2005-01-11 03:45 | 2005-01-12 07:00 | 200 | 100000 | 0 | 100000 | 31563 Ortega Highway | San Juan Capistrano | 92675 | OC | Force Main | 0 | 0 | LINE BREAK | Unable to locate break due to flooding local creeks. Flow is being bypassed to sewer with temporary pipelines and pumper trucks until we can locate the break. | Temporary bypass with invasion lines and pumper trucks. | Y | Y | Y | San Juan Creek | Pacific Ocean |  | Y | Y | Y | Unknown |  | OES #05-0326. Actual start time of break is unknown. The station was checked at 3:00 am on 1/11 and was fine. The bridge washed out at 3:45 am on the 11th, but the station did not lose pressure until the early morning of 1/12. The spill estimate assumes a start time coinciding with the bridge wash out.
045006 | Quarterly Report | 2005-01-31 08:30 | Dave Seymour | (949) 459-6540 | Santa Margarita Water District | Santa Margarita Water District | 2005-01-31 07:45 | 2005-01-31 08:05 | 10 | 200 | 200 | 0 | Applegate Manhole 784.53 | Mission Viejo | 92690 | OC | 8-inch Sewer Line | 0 | 0 | OTHER | Flow monitor's restraining band broke and slipped into the channel. | Removed the monitor | N | N | N | None | None | Vactor | Y | N | N
045005 | FAX (858) 571-6972 | 2004-11-25 13:48 | Steve Francis | (949) 459-6539 | Santa Margarita Water District | Santa Margarita Water District | Unknown | 2005-11-25 12:30 |  | 0 | 0 |  | 22202 Brookpine | Mission Viejo | 92691 | OC | Sewer Lateral | 0 | 0 | OTHER | Four-inch sewer lateral was not connected to the main during original construction (approximately 17 years old). Flow passed through soil to sewer main. An undetermined amount of sewage percolated through the soil. | The contaminated soil was removed and the lateral was connected with a new section of pipe. | N | N | N | None | None | Sewage perculated into soil (subsurface) | Y | Y | N | N/A | 0 | OES #046154 The overflow start time, end time, flow rate, and volume are unknown. The overflow was subsurface. Approximately 1/4 yard of contaminated soild was removed.
045001 | FAX 858-571-6972 | 2004-07-20 16:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2004-07-19 16:30 | 2004-07-19 16:40 | 2 | 20 | 20 | 0 | 25412 Sea Bluff | Dana Point | 92629 | OC | MANHOLE NO. 1109F | 0 | NONE | DEBRIS | Crews found asphalt, concrete and rocks that had been discarded into MH | District crews responded by laying down the spill containment mat with sand bags and a combination truck at the nearest storm drain. Debris traps were set at 2 downstream manholes. Crews vacuumed and jetted the main lines from manhole 1109G to 1109F and 1109E, no more debris was found in the system. Crews washed down street and vacuumed flow with combination truck. Water hydrant was flushed for 5 minutes. Crews set the combination truck at the Del Obispo street diversion gate valve site and vacuumed 1000 gallons for preventative measures. | N | Y | N | n/a | n/a | Storm drain - flushed and recovered | Y | N | N | n/a | 0
045002 | FAX 858-571-6972 | 2004-12-13 11:35 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2004-12-12 09:50 | 2004-12-12 10:10 | 3 | 60 | 60 | 0 | 26752 Calle Almanza | Capistrano Beach | 92624 | OC | MANHOLE NO. 458 | 0 | NONE | ROOTS | District crew found a small amount of sewage flowing out of MH #458 pick holes. Crew removed a root mass of approx. 4" in diameter and 3" in length. Root mass of this size is indicative of private sewer lateral cleaning. | SCWD mainline in this area was last cleaned out on April 1, 2004. To try to determine exact origin of root mass, SCWD video crew inspected lines and sewer lateral connections from MH #457 to #459. Video crew found two sewer laterals impacted with roots at a connection to main. Homeowners have been notified with door hangers that their lateral needs to be cleaned due to root intrusion and they must contact SCWD prior to cleaning so that SCWD could respond by placing a debris trap downstream to prevent future sewer overlfows of this kind. | N | N | N | n/a | n/a | Street surface. | Y | N | N | n/a | 0
045003 | FAX 858-571-6972 | 2005-01-03 12:45 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-01-03 11:45 | 2005-01-03 12:25 | 35 | 1400 | 75 | 1325 | 31871 Circle Drive | Laguna Beach | 92651 | OC | Clean out at sewer tunnel drop MH 1166 | 0 | NONE | BLOCKAGE | During a routine inspection by the District's lift station crew, the crew discovered wastewater flowing out of a manhole into an adjacent storm basin. The crew found a solid object blocking the sewer pipeline. After several attempts with the steel rod from a cleaning machine, the blockage was cleared and the normal flow resumed. | The source and type of blockage is unknown and since it was broken loose and forced into the larger 24" sewer pipe in the sewer tunnel, it was almost impossible to identify what the blockage was. These lines were recently cleaned in 11/04 as part of the SCWD's annual maintenance program and the video inspection indicates that all pipes and manholes are in good condition with no obstructions. There had been substantial rain and some localized flooding in the general upstream area of this SSO and it is possible that storm water run off was diverted into the SCWD sewer system manhole in this area by unknown parties. Debris from stormwater runoff could have entered the sewer line and caused the blockage. SCWD crews will install locking MH lids at MH 1154, 1092 and 1153 to prevent future SSO's of this type. | Y | Y | Y | Pacific Ocean | n/a | n/a | Y | Y | Y | Seacliff Drive to 1000 steps County Beach | 3
045005 | FAX 858-571-6972 | 2005-03-23 11:55 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-03-21 | 2005-03-23 08:30 |  | 30 | 30 | 0 | 34036 Amber Lantern | Dana Point | 92629 | OC | Lateral line | 0 | NONE | ROOTS | Property owner's sewer lateral was clogged with heavy root buildup beginning approximately one foot up from the sewer main. Cap removed from cleanout and sewage coming out of it. | After putting a debris trap downstream to catch roots, SCWD crews ran jetter in main line. SCWD crews retrieved roots in the main line that came from the service lateral cleaning. | N | N | N | n/a | n/a | Overflow saturated into the ground around the cleanout. | Y | N | N | n/a | 0 | Private System Overflow Incident | x
045004 | FAX 858-571-6972 | 2005-01-07 19:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 1//7/2005 19:30 | 2005-01-07 20:11 | 15 | 600 | 0 | 600 | 34281 Camino El Molino | Capistrano Beach | 92624 | OC | MH 331 | 0 | NONE | BLOCKAGE | Blockage in main line caused overflow at Manhole 331. Crews retrieved 2-1/2 gallons of debris and roots out of sewer line at Manhole 332. | Crews completed additional video and visual inspection from MH 330 to 331 to 333 and found all lines intact and free of any obstructions. It is suspected that a plumber pushed roots and debris into SCWD sewer main while maintaining a private lateral. SCWD is preparing to issue letters with photographs of root impacted laterals to homeowners requesting them to clean their laterals and notify SCWD prior to work so the District can collect roots and debris at downstream manhole to prevent further SSO's. This process will be implemented in phases and a pilot program is planned tentatively for March 2005 when the first 35 homewoners will be notified. | Y | Y | Y | Pacific Ocean | n/a | n/a | Y | N | Y | 35051 Beach Road - 100 yards from each side of strom drain discharge into ocean | 4
048008 | Victor Vasquez | 2004-08-31 | Kris Hanberg | 949-858-0277 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2004-08-08 07:00 | 2004-08-08 09:15 | 3 | 414 | 0 | 414 | 21014 Plano Trabuco Road | Trabuco Canyon | 92679 | OC | n/a | 0 | n/a | Line Break | 1" lateral to Air Vac sprung a hole | Replaced lateral and coverd with sand | N | Y | Y | Tieras creek | none | Tieras creek | Y | N | N | N/A | 0
041009 | Victor Vasquez | 2004-10-20 | Kris Hanberg | 949-858-0277 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2004-10-20 08:40 | 2004-10-20 08:50 | 120 | 1200 | 0 | 1200 | 21494 Heritage Drive | Trabuco Canyon | 92679 | OC | Heritage Lift Station | 0 | n/a | Infiltration | Heavy rains | Look at increasing Pump GPM | y | n | y | Dove Lake | San Juan Creek | Ocean | y | y | n | N/A | 0
045003 | VOICE | 2/22/05 0800 | Gene Palop | 858-451-7837 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2005-02-21 14:25 | 2005-02-21 14:45 | 45 | 900 | 0 | 900 | 10605 Rancho Bernardo Rd | San Diego | 92127 | SD | Fire House Pump Station | 0 | n/a | POWER FAILURE | A power failure caused the pump VFD to trip and also lost communication with the main plant scada computer. The power failure at the main plant created problems with the main scada computer causing it to freeze operations. When the second scada computer took control, it strted sending out lot of alarms to the duty pager, which we responded to. | The pump VFD was inspected and tested for proper operation. The communication equipment was inspected and tested for normal operation. Both main and backup scada computers we rebooted and are working properly. | Y | Y | Y | Storm Drain Culvert | San Dieguito River | San Dieguito Lagoon / Pacific Ocean | y | y | N | na | 0
045001 | Bryan Ott (858) 637-5589 | 2004-07-22 15:00 | Chad Davisson | (760) 420-6885 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2004-07-22 08:45 | 2004-07-22 12:00 | 40 | 7750 | 7500 | 250 | 16106 4S Ranch Parkway | San Diego | 92127 | SD | Sewer Manhole | 0 |  | DEBRIS | Rocks and construction related debris resulted in an obstruction within this manhole. | Overflow occurred in spill contained area. Contained wastewater was removed by vacuum truck and disposed of at the adjacent pump station. Sewer line to be cleaned and video conducted. | N | N | N | none | none | A small amount of sewage soaked into the ground, as the containment basin was not lined | N | N | N |  |  | This overflow occurred within a spill containment area. No sewage entered any surface water or storm drain. We estimate that no more than 250 gallons of residual sewage soaked into the ground within the containment area.
045002 | Bryan Ott (858) 637-5589 | 2004-09-08 10:30 | Chad Davisson | (760) 420-6885 | Olivenhain Municipal Water District | Olivenhain Municipal Water District | 2004-09-08 08:05 | 2004-09-08 09:00 | 15 | 825 | 825 | 0 | Dove Creek Road | San Diego | 92127 | SD | Sewer Manhole | 1 | 2004-07-22 | BLOCKAGE | Gravel and construction debris caused blockage in sewer line | Dispatched vac trucks to remove sewage within manholes. Sewage was taken to sewer lift station. Used vactor truck to clear blockage. Washed area with chlorinated water using water truck. Videoed sewer line to confirm clear. | N | Y | N | none | none | sewer lift station | N | N | N |  |  | Release was collected via tank truck and disposed of at a sewer lift station.
045001 | Brian Ott - Fax 858-571-6972 | 2004-07-09 12:20 | Jim Miller | 760-839-4323 | City of Escondido | City of Escondido | 2004-07-09 11:30 | 2004-07-09 12:30 | 0.42 | 25 | 25 | 0 | 1750 S. Juniper St. | Escondido | 92025 | SD | Private cleanout | 0 | N/A | ROOTS | Private discharge due to lack of maintenance. | Private plumber cleaned the sewer lateral. The Pretreatment Inspector may issue a Notice of Correction to the property owner. | N | N | N | N/A | N/A | Recovered & returned to the Collection System. | Y | N | N | N/A |  |  | x
045003 | Brian Ott - Fax 858-571-6972 | 2004-08-24 13:30 | Jim Miller | 760-839-4323 | City of Escondido | City of Escondido | 2004-08-24 08:00 | 2004-08-24 10:12 | 2 | 264 | 25 | 239 | 1435 Simpson Way | Escondido | 92026 | SD | Private cleanout | 0 | N/A | UNKNOWN | Private discharge due to lack of maintenance. | A Notice of Correction will be issued to the property owner. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | N | N | N/A |  |  | x
045004 | Brian Ott - Fax 858-571-6972 | 2004-09-13 16:00 | John Vaught | 760-838-4323 | City of Escondido | City of Escondido | 5/6/04 N/A | 2004-09-13 13:00 | 0.11 | 20800 | 100 | 20700 | 823 N Citrus St. | Escondido | 92026 | SD | Private resident waste line connested | 0 | N/A | OTHER | Private service lateral was illegality connected to the city's storm system. | City Pretreatment Inspector and Code Enforcemant Officer are having the property owner termiate the connection ASAP. City crews televised and cleaned the storm pipe. | N | Y | Y | Escondido Creek | San Elijo Lagoon |  | Y | Y | N | N/A |  |  | x
045005 | Fax- Brian Ott 858-571-6972 | 2004-10-04 13:30 | Romero Gonzalez | (760) 839-4323 | City of Escondido | City of Escondido | 2004-10-03 14:40 | 2004-10-03 15:30 | 1 | 50 | 50 | 0 | 1408 E. Valley PKWY. | Escondido | 92025 | SD | Grease interceptor | 0 | 0 | GREASE | Grease interceptor at El Pollo Loco wasn't working property, backed-up and discharged to parking lot and gutter. | Pretreatment Division was notified and may issue a Notice of Correction. | N | N | N | None | None | City crew vacuumed wastewater and discharge to sanitary sewer. | Y | N | N | N/A | 0 |  | x
045006 | Fax- Brian Ott 858-571-6972 | 2004-11-12 15:22 | Jim Miller | (760) 839-4323 | City of Escondido | City of Escondido | 2004-11-08 10:00 | 2004-11-12 16:00 | 0.145 | 630 | 30 | 600 | 626 Inspiration Lane | Escondido | 92025 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Lack of maintenance, roots. | Pretreatment Division was notified and may issue a Notice of Correction. The property owners responsibilities were explained. | Y | Y | N | None | None | Ground absorption | Y | N | N | N/A | 0 |  | X
045007 | Fax- Brian Ott 858-571-6972 | 2004-11-15 10:30 | Romero Gonzalez | (760) 839-4323 | City of Escondido | City of Escondido | 2004-11-13 21:00 | 2004-11-14 15:30 | 2.35 | 2610 | 300 | 2310 | 505 W. 5th. St. | Escondido | 92025 | SD | City Sewer Manhole #6680 | 0 | 0 | GREASE | Main line overflow due to excessive grease. | Pretreatment Division was notified that our main line was full of grease after the CCTV inspection. | Y | Y | Y | Escondido Creek | San Elijo Lagoon | N/A | Y | Y | N | N/A | 0
045008 | Fax- Brian Ott 858-571-6972 | 2004-11-24 14:10 | Mike Schultz | (760) 839-4323 | City of Escondido | City of Escondido | 2004-11-24 10:30 | 2004-11-24 11:30 | 5 | 300 | 300 | 0 | 2108 Flint Ave. | Escondido | 92025 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Debris in private lateral. | Contractor replaced the sewer lateral on 11/29/2004. | N | N | N | None | None | Wastewater was contained and went to soil. | Y | N | N | N/A | 0 |  | X
045009 | Fax- Brian Ott 858-571-6972 | 2004-12-13 16:20 | Bill Kutarnia | (760) 839-4323 | City of Escondido | City of Escondido | 2004-12-13 15:05 | 2004-12-13 15:15 | 1 | 10 | 10 | 0 | 340 N. Escondido Blvd. | Escondido | 92025 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Private overflow due to lack of maintenance. | Customer called a plumber. | N | Y | N | None | None | Wastewater recovered from dry catch basin. | Y | N | N | N/A | 0 |  | X
045010 | Fax- Brian Ott 858-571-6972 | 2004-12-20 13:30 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2004-12-17 13:00 | 2004-12-17 13:50 | 1 | 50 | 50 | 0 | 925 Ball St. | Escondido | 92025 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Unknown, private system | Pretreatment Division was notified and property owner was informed of their responsibilities. A Notice of Correction may be issued. | N | N | N | None | None | Recovered and returned to sanitary sewer. | Y | N | N | N/A | 0 |  | X
045012 | Brian Ott Fax 858-571-6972 | 2005-01-20 16:30 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2005-01-20 14:27 | 2005-01-20 15:12 | 10 | 450 | 120 | 330 | 1366 W. Valley Pkwy. | Escondido | 92025 | SD | City sewer manhole 5121 | 0 | 0 | DEBRIS | Crew reported bags, paper & other debris. Some grease. | Pretreatment Division was notified of the situation. The sewer main will be inspected to determine a course of action. | N | Y | Y | Escondido Creek | San Elijo Lagoon/Pacific Ocean |  | Y | N |  | N/A | 0
045013 | Brian Ott Fax 858-571-6972 | 2005-02-18 10:30 | Jason Medeiros | (760) 839-4599 | City of Escondido | City of Escondido | 2005-02-28 09:30 | 2005-02-28 10:45 |  |  |  |  | 211 Greenview Rd | Escondido | 92027 | SD | Private septic system | 0 | 0 | PRIVATE PROPERTY | City of Escondido crews responded to a failing septic system outside their jurisdiction. | City crews asked the tenant to refrain from using the system and directed the landlord to contact a pumping service. Staff set up a location to vacuum any waste leaving the property until the pumping service arrived. Clay Clifton was contacted for guidance and ststed he would dispatch a local land use inspector from DEH staff to investigate. | Y | N | N | N/A | N/A | Absorbed to soil | Y | N |  | N/A | 0 |  | x
045014 | Brian Ott Fax 858-571-6972 | 2005-02-22 15:17 | Ron Canfield | (760) 839-4599 | City of Escondido | City of Escondido | 2005-02-21 10:55 | 2005-02-21 12:10 | 150 | 11250 | 0 | 11250 | Metcalf St & Mission Ave. | Escondido | 92025 | SD | City sewer manhole 4921 | 0 | 0 | DEBRIS | Debris in main line created blockage. | City staff will inspect the main line in an effort to determine what type of debris caused the blockage. This line was last cleaned on 1/5/05. | Y | Y | Y | Escondido Creek | San Elijo Lagoon/Pacific Ocean |  | Y | Y |  | harmony Grove Rd. Country Club Dr. Elfin Forest Rec. Park | 7
045016 | Brian Ott Fax 858-571-6972 | 2005-03-16 16:30 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2005-03-16 06:30 | 2005-03-16 10:00 | 0.19 | 40 | 40 | 0 | 1742 E. Valley Pkwy. | Escondido | 92027 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Private system, no evidence of what caused the blockage. | City Pretreatment Inspector was notified and may issue a Notice of Correction. | N | Y | N | N/A | N/A | Vacuumed and returned to sanitary sewer. | Y | N |  | N/A | 0 |  | x
045017 | Brian Ott Fax 858-571-6972 | 2005-03-22 14:00 | John Vaught | (760) 839-4323 | City of Escondido | City of Escondido | 2005-03-22 10:40 | 2005-03-22 11:20 | 3 | 120 | 120 | 0 | 330 N. Juniper St. | Escondido | 92025 | SD | Private cleanout | 0 | 0 | PRIVATE PROPERTY | Grease and other debris seem to be the issue. | City Pretreatment Inspector was notified and may issue a Notice of Correction. | N | Y | N | N/A | N/A | Vacuumed from storm pipe and returned to sanitary sewer.. | Y | N |  | N/A | 0 |  | x
045019 | Fax Brian Ott 858-571-6972 | 2005-06-15 15:30 | John Vaught | 760-839-4323 | City of Escondido | City of Escondido | 2005-06-15 10:30 | 2005-06-15 14:30 | 3 | 730 | 730 | 0 | 442 W. 4th Ave. | Escondido | 92025 | SD | Private cleanout | 1 | 2004-11-13 | PRIVATE PROPERTY | Unknown - Private system | Cioty Pretreatment Inspector is investigating and may iddue a Notice of Correction to the property manager | N | N | N | None | None | Wastewater pooled in low areas of the alley and recovered by city crew and returned to sanitary sewer. | Y | N |  | N/A |  | Affected area was disinfected by city crew. | x
045001 | 1(858)571-6972 | 2004-07-28 03:30 | Serafin Perez | (619) 397-6031 | City of Chula Vista | PRIVATE PROPERTY | 2004-07-27 18:00 | 2004-07-27 21:30 | 20 | 18600 | 1200 | 17400 | 710 E St. | Chula Vista | 91910 | SD | Private Sewer Laterals (4) Four Inch Cleanouts | None | None | PRIVATE PROPERTY | Roots in private sewer lateral. | Advise asst. property manager to have a maintenance schedule with a plumber to avoid reoccurrences. | No | Yes | Yes | G St. Marina | None | G St. Bay Area | Yes | Yes | Y | G St. Marina | 3 | City was notified at 5:00 pm. City crew started the containment at 6:00 pm at the E St. trolley station catch basin. Asst. manager turned off water supply to the Inn from 8:00- 9:00. Sewer water leaking from cleanouts. Assumptions: Overflow started at approx. 6:00 am. Sewer water was flowing from cleanouts, estimated at 20 GPM. | x
045002 | 1(858)571-6972 | 2004-08-31 01:55 | Mark Sanchez City of Chula Vista Public Works Supervisor | (619)397-6000 | City of Chula Vista | City of Chula Vista | 2004-08-30 19:30 | 2004-09-01 12:30 | 13 | 35195 | 1500 | 33694 | N.E Hunte Pkwy. & Yosemite Dr. | Chula Vista | 91915 | SD | Sewer Manhole/Access Port | 0 | N/A | BLOCKAGE | After plug was broken, two rubber test plugs were pulled out of the sewer main. It appears that concrete was deposited into the flow line from when a contractor adjusted the manhole ring and cover to grade. A large amount of grease and paper contributed to the stoppage as well. | Stoppage was removed, sewer main flushed. City staff removed concrete from manhole bench and flow line. Sewer main lines were hydraulically cleaned and vacuumed up and downstream from sewer stoppage. Met with city inspector and discuss preventive measures, contractor will clean and televise up an down stream as well. | No | Yes | Yes | Strom Drain/ Catch Basin | Salt Creek Basin | Hawthorne Creek & Otay Lakes Rd. | Yes | Yes | Y | East of Hunte Parkway North of Otay Lakes Rd. | 5 | Assumptions: 211 single-family residences connected up to that sewer main. 75% occupancy in new subdivision. Approximately 158 single-family residences are operational. Assuming each house uses approximately 198 gallons per day. Assuming the spill was 27 hours. Assuming 8.25 gallons per hour per single family resident. 1500 gallons recovered.
045003 | 1(858)571-6972 | 2004-09-07 16:30 | Serafin Perez | (619)397-6031 | City of Chula Vista | PRIVATE PROPERTY | 2004-09-07 10:00 | 2004-09-07 12:00 | 10 | 1200 | 1200 | 0 | 512 Woodlawn St. | Chula Vista | 91910 | SD | Overflow through apartment private 4'' sewer c/o | 0 | N/A | PRIVATE PROPERTY | Cause of blockage is unknown. | Apartment maintenance personnel turned off water to the apartments until blockage was removed. City staff dammed off private catch basin and contained private sewer spill. A Notice of Violation (Cease and Desist, Clean and Abate Order) by NPDES Inspectors will be issued to property owners. | No | Yes | No | None | None | Concrete storm drain channel between H & I St. Storm drain channel was dammed at I St. and vacuumed. | Yes | N/A | N | N/A | N/A | Public Works Dispatch was notified of spill at 11:30 am. Containment began at 12:00 pm at the private catch basin at the apartment entrance located at the Northwest corner of the property. Apartment maintenance staff informed city staff the spill began at 10:00. Water was turned off at the apartments at 12:00 PM. City staff estimated 10-gpm overflow. City staff dammed concrete strom channel at I Street and directed it to where it could be vacuumed up by combination vehicle. City staff washed down channel and swept water to combination vehicle. | x
045001 | Quarterly Report | 2004-09-01 13:05 | K LeMoine | 522-7898 | City of Coronado | City of Coronado | 2004-08-31 11:15 | 2004-08-31 13:15 | 62.5 | 7500 | 7500 | 0 | 343 F Avenue | Coronado | 92118 | SD | Water Main Line | 0 |  | LINE BREAK | Break in water main supply line | City crews used Vactor to suck up potable water, protected storm drain inlet. CalAm Water repaired water main | N | N | N | None | None |  | Y | N | N |  |  | Reported to DEH as a precaution. No water into storm drain.
045002 | Quarterly Report | 2004-09-07 12:20 | S Jones | 522-7317 | City of Coronado | City of Coronado | 2004-09-07 11:00 | 2004-09-07 11:30 | 0 | 3 | 3 | 0 | 1770 Ave del Mundo | Coronado | 92118 | SD | Storm Drain Inlet | 0 |  | OTHER | Privately owned vehicle spilled diesel fuel, which ran into storm drain inlet | Recovered all fuel using Vactor, jetted line 160 feet | N | Y | N | None | None |  | Y | N | N
045003 | Voicemail (858) 467-2952 | 2004-09-08 16:15 | J Ramirez | 522-7898 | City of Coronado | City of Coronado | 2004-09-08 14:25 | 2004-09-08 15:00 | 0 | 13 | 0 | 13 | 1515 Second Street | Coronado | 92118 | SD | Storm Drain line | 0 |  | BLOCKAGE | Private property car wash area drain clogged, cleared and released standing water to storm drain | Car was area closed, drain line connected to sewer system | N | Y | Y | San Diego Bay | None |  | Y | N | N
045004 | Quarterly Report | 2004-09-13 08:46 | M Dias | 522-7380 | City of Coronado | City of Coronado | 2004-09-13 20:40 | 2004-09-13 22:30 | 0 | 1 | 1 | 0 | 301 Orange Avenue | Coronado | 92118 | SD | Sewer Main Line | 0 |  | DEBRIS | Mop remains stuck in sewer main line | Removed debris, cleaned up small amount of sewerage puddled on manhole cover. | N | Y | Y | None | None |  | Y | N | N
045005 | Quarterly Report | 2004-09-27 20:10 | K LeMoine | 5227898 | City of Coronado | City of Coronado | 2004-09-26 21:37 | 2004-09-27 02:00 | 0.7 | 150 | 150 | 0 | 1112 Second Street | Coronado | 92118 | SD | Sewer Lateral | 0 |  | ROOTS | Roots in private lateral caused overflow, interecepted by diversion structure | Diverted to sewer system at First/Orange diversion structure. Cleaned street and storm drain inlet. | N | Y | N | None | None |  | Y | N | N
045001 | Quarterly Report | 2004-08-02 17:15 | Victor Sturm, Paul Thomas, David Zilberberg | (858) 755-3294 | City of Del Mar | City of Del Mar | 2004-08-02 17:00 | 2004-08-03 17:15 | 2 | 30 | 30 | 0 | 1925 Ocean Front | Del Mar | 92014 | SD | Private lateral blockage at 1925 Ocean Front Street | 0 | N/A | PRIVATE PROPERTY | Private lateral blockage at 1925 Ocen Front Street | Property owner called Pacific Drain Service and they rodded their lateral. Public Works employee on site, City main was clear, PW employee vacuumed all overflow + wash down and returned it to the main (City main was last rodded on 6/4/04). | N | N | N | none | none | Captured all sewer overflow and wash water at 1925 Ocean Front Street and returned it to the main | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at 1925 Ocean Front Street. | x
045001 | David Hanson | 2004-08-23 08:45 | Patrick Jackson | (619) 441-1658 | City of El Cajon | City of El Cajon | 2004-08-23 07:40 | 2004-08-23 08:00 | 100 | 2000 | 400 | 1600 | 800 Blk. El Cajon Blvd. | El Cajon | 92020 | SD | 09-088 | 0 | N/A | DEBRIS | A broken Manhole step was caught in line, restricting flow. | Removed broken manhole step from line. | N | Y | Y | County Ditch | Forrester Creek | San Diego River | Y | Y | N | N/A | 0 | This section of pipe was replaced with "burst pipe" approx. five years ago.
045001 | Quarterly Report | 2004-09-20 17:00 | Sheriff Department | (858)565-5200 | City of Imperial Beach | City of Imperial Beach | 2004-09-20 17:00 | 2004-09-20 17:45 | 1 | 40 | 40 | 0 | Silver Strand Plaza | City of Imperial Beach | 91932 | SD | Clean Out Silver Strand Plaza | 0 | None | BLOCKAGE | The Vactor crew cleaned the line affecting the Silver Stand Plaza in the morning as per the monthly jetting list. They were not aware that when cleaning this line, they needed to continue the shot until they reached fifth Street. | The Vactor crew has been briefed on cleaning this line and the importance of continuing the cleaning to Fifth Street. | N | N | N | N/A | N/A | Vactor to Sewer | N | N | N | N/A | 0 | None
045002 | David Hanson 858-571-2724 | 9/28/2004 0945 | I.B. Lifeguards | (619)423-0208 | City of Imperial Beach | City of Imperial Beach | 8/29/2004 0930 | 8/28/2004 10000 | 2 | 60 | 0 | 60 | Imperial Beach Pier | City of Imperial Beach | 91932 | SD | I.B. Pier Clean Out | 0 | None | BLOCKAGE | The lateral was spilling intermittently. The cause of the blockage unknown. | The lifeguards noticed drips from a clean out under the pier. The lifeguards called the sewer emergency pager and the sewer duty man ordered the restroom, restaurant and lifeguard tower restroom to be closed. The sewer crew used a Vactor truck to attempt to clear the blockage and were unsuccessful. A plumber was called and a smaller trailer jetter was used to alleviate the blockage. The spill occoured over the Pacific Ocean, so there was no way to recover the sewerage. The lifeguards have posted signage and it will remain posted until a clean water sample is obtained. | N | N | Y | Pacific Ocean | N/A | N/A | Y | N | Y | North and South of Pier | 3 | None
05-01 | N/A | N/A | N/A | N/A | City of La Mesa | City of La Mesa | 08/15/04 16:30 | 08/15/04 17:00 | 1 | 40 | 0 | 40 | La Mesa Blvd. & Normal Ave. | La Mesa | 91941 | SD | 4" Concrete Pipe | 0 | N/A | BLOCKAGE | Paper towels blocked the line | Cleared the blockage | N | n | N | N/A | N/A | Dried up on Street | N | N | N | N/A | 0
045001 | Victor Vasquez 858-467-2952 | 2004-07-26 09:30 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2004-07-26 08:30 | 2004-07-26 12:00 | 225 | 47250 | 25200 | 22050 | Main St | Lemon Grove | 91945 | SD | 576-21-08 to 07 | 0 | 0 | VANDALISM | Sealed cover of MH broken open. Rocks, sandbags, debris thrown into mainline causing major obstruction in 10" line. | Due to large rocks & sandbags lodged into pipe, mainline was removed & replaced. MH lid to be resealed + chain debice over lid. | N | N | N | none | none | Effluent settled within the San Altos drainage easement | Y | N | Y | Main St between San Passqual l& Beryl St | 7 | Photos available
045002 | Victor Vasquez FAX | 2004-08-03 12:26 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2004-08-02 11:03 | 2004-08-02 16:45 | 50 | 750 | 190 | 560 | Canton Dr & Lemon Grove Ave | Lemon Grove | 91945 | SD | 576-34-01 | 1 | 2004-07-26 | VANDALISM | additional rocks & debris that excaped detection during repair work of 7-26-04 vandalism | Jettted and videoed line from spill area to S City limits. Consulted on site w/City of SD sewer superintendent re meter station & downstream lines in City of SD | N | N | N | none | none | Absorbed in dirt area of open drain ditch. | Y | N | N | none | 0 | Area of spill not accessable by the public
| FAX to David Hanson | 09/13/04 10:30AM | Joe Smith | 619 336-4587 | City of National City | City of National City | 2004-09-12 06:30 | 2004-09-12 09:00 | 10 | 1500 | 0 | 1500 | 0-99 BLK 12th @ A avenue | National City | 91950 | SD | MH # 337 | 0 | N/A | DEBRIS | Partial blockage in 6 inch main caused by rags from an unknown source. | Blockage removed and all affected areas were cleaned & sanitizes. All water used to clean was recoved and put into the sewer system. | N | Y | N | storm drain only | none | storm drain | Y | N | N | N/A | 0 | The affected is a closed concrete system running undergroung. The location of the strom drain is approximately 2 miles from the San Diego bay.
045001 | Voice Mail | 08/07/04 1910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 08/07/04 1445 | 08/07/04 1545 | 5 | 300 | 300 | 0 | 4406 Kittiwake Street | Oceanside | 92056 | SD | Manhole | 0 |  | DEBRIS | Contractor re-paved the streets and pushed asphault and concrete into the sewer line. | Entry was made to remove debris and contact was made with the offending contractor. | N | Y | N | None | none | Full recovery from Stormdrain. | Y | N | N |  |  | Spill was chased down stream to Old Grove Road and fully recovered.
045002 | Brian | 08/20/04 1530 | Isaac Richardson | 7604355840 | City of Oceanside | City of Oceanside | 08/20/04 0835 | 08/20/04 0850 | 20 | 300 | 300 | 0 | 3747 Vista Campana South | Oceanside | 920545 | SD | Manhole | 0 |  | ROOTS | Roots blocking main caused overflow. | Cleaned line with rodder and will CCTV line. | N | Y | N | None | none | Full recovery from Stormdrain. | Y | N | N |  |  | City crews cleaned storm drain and recovered 100%.
045003 | Victor | 09/16/04 0807 | Mark Patnode | 7604355840 | City of Oceanside | City of Oceanside | 09/15/04 1627 | 09/15/04 1638 | 1.5 | 20 | 20 | 0 | 2900 Block of Farel | Oceanside | 92054 | SD | Manhole | 0 |  | ROOTS | Roots in City line caused overflow. | Line was cleaned by rodder crew. | N | Y | N | None | None | Full recovery from Stormdrain. | Y | N | N |  |  | This 8 inch line was put on root control with Pacific Sewer Maintenance Corp. in Jul04. Line was treated with Vaporooter in Aug04. Line will be TV'd to see if dead roots were cause.
045004 | Victor Vasquez | 09/30/04 0910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 09/29/04 1255 | 09/29/04 1305 | 5 | 200 | 200 | 0 | 3766 Mission Avenue | Oceanside | 92054 | SD | Private Cleanout | 0 |  | PRIVATE PROPERTY | 6-inch private lateral belonging to Shopping Center. | Three vactors on site to recover spill. Code Enforcement called. | N | N | N |  |  | Full recovery from Parking Lot. | Y | N | N |  |  | City handled spill until property management's plumber cleared stoppage around 16… | x
045005 | Victor Vasquez | 09/30/04 0910 | Jeremy Kemp | 7604355842 | City of Oceanside | City of Oceanside | 09/29/04 1255 | 09/29/04 1305 | 10 | 400 | 150 | 250 | 1906 Oceanside Blvd. | Oceanside | 92054 | SD | Private Cleanout/Grease Trap | 0 |  | PRIVATE PROPERTY | Small private lateral belonging to Shopping Center. | City damed spill with sand bags until vactor arrived. Called Code Enforcement. | N | Y | Y | Loma Alta Creek |  | Flows pumped out of Loma Alta Slough into La Salina WWTP. | Y | N | N |  |  | Full recovery not possible. Spill contained in Flood Control Channel to Slough, but no public contact. Private plumber cleared stoppage 2130 hours. | x
045001 | Fax | 2004-08-23 10:00 | David Vigliotti | 858-668-4719 | City of Poway | City of Poway | 2004-08-20 08:00 | 2004-08-20 08:15 | 3 | 45 | 25 | 20 | 13608 Pomerado Rd | Poway | 92064 | SD | 6" private lateral | 0 |  | PRIVATE PROPERTY | Roots and possible separation on private side of sewer system was cause of discharge. Private 6" sewer cleanout is located approx. 20 ft from curb area. | Private cleanout was rodded and cleared; containment barriers in three locations were set up and spill vacuumed with Vactor. Storm drain pipes and two collection boxes were jet-rodded and Vactored as additional measure. Area downstream within concrete channel has limited public access; no signs posted. | N | Y | Y | Drop inlet on Pomerado Rd | Pomerado Channel |  | Y | N | N |  |  | Apartment complex manager was notified of sewer lateral damage on private side of system. Customer contacted private contractor while City crews on-site; area was being prepped for repairs when crews left. | x
034008 | Brian Kelly | 2004-07-19 16:40 | Anne Briggs | 951-928-3777 | Eastern Municipal Water District | Eastern Municipal Water District | 2004-07-19 15:16 | 2004-07-19 16:14 | 25 | 1450 | 300 | 270001150 | Front Street 5th and 6th | Temecula | 92592 | RV | Manhole | 0 | 0 | GREASE | Grease caused 2 manholes to backup | Investigate grease traps at restaurants and clean sewer lines as necessary | N | Y | Y | Murrieta Creek | n/a | n/a | Y | Y | Y | Along creek | 5
045001 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 8/30/2004 10:50 | 8/30/2004 11:00 | 1 | 10 | 5 | 5 | 224 O'Hearn Drive | Fallbrook | 92028- | SD | Cleanout | 0 |  | PRIVATE PROPERTY | Roots from nearby trees. | Rodded lateral, and root-x'd line. | N | N | N | None | None | Soaked into ground around cleanout box. | N | N | N |  | 0 | PRIVATE SEWER - COURTESY NOTIFICATION. | x
045002 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 9/4/2004 11:30 | 9/4/2004 12:05 | 3 | 105 | 0 | 105 | 820 Cookie Lane | Fallbrook | 92028- | SD | Cleanout | 0 | NA | ROOTS | Roots in mainline. | Flushed mainline, found blockage at 36 feet. | N | N | N | None | None | Along side of road in field. | Y | N | N |  | 0 | Disinfected along the roadway where it traveled into field.
045003 | QUARTERLY REPORT |  |  |  | Fallbrook Public Utilities District | Fallbrook Public Utilities District | 9/30/2004 08:36 | 9/30/2004 11:30 | 0.5 | 91 | 0 | 91 | 400 W. Fallbrook Street | Fallbrook | 92028- | SD | Cleanout | 0 | NA | PRIVATE PROPERTY | Blockage occurred from past construction. | Located cleanout and removed blockage. Also flushed main line and TV'd main line. | N | N | N |  |  | Around cleanout and soaked into the ground. | Y | N | Y | Around contaminated area. | 3 | COURTESY NOTIFICATION. School District is going to remove the soil that was affected. | x
045001 | VOICE MAIL | 2004-09-25 15:00 | JOHN PASTORE | (760) 479-4121 | Rancho Santa Fe Community Services District | Rancho Santa Fe Community Services District | 9/25/04 2330 | 9/25/04 1230 | 5 | 670 | 0 | 670 | El Camino Real | Rancho Santa Fe | 92067 | SD | ECRFM-01 | 0 | NA | Line Break | A coupling on the 6-inch force main pulled apart causing a leak around the gasket. | The leaking pipe was shut down within 1-hour of notification. The spill area was immediately vactored and 22,500 gallons of water in the creek was pumped a d hauled away by tanker truck to the sewer system. The area was immediately posted. The ppe reparis have been completed and tested. | N | N | Y | Drainage creek at El Camino Real and La Orilla. | None | Recovered and trucked to the sewer treatment plant for disposal. | Y | Y | Y | Along El Camino real & La orilla | Still posted | Because the spill entered directly into the drainage creek, there was already standing water in the creek. Therefore, we pumped out and disposed of 32 times the amount of the sewage spill amount for extra precaution.
045001 | FAX 858-571-6972 | 2004-07-20 16:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2004-07-19 16:30 | 2004-07-19 16:40 | 2 | 20 | 20 | 0 | 25412 Sea Bluff | Dana Point | 92629 | OC | MANHOLE NO. 1109F | 0 | NONE | DEBRIS | Crews found asphalt, concrete and rocks that had been discarded into MH | District crews responded by laying down the spill containment mat with sand bags and a combination truck at the nearest storm drain. Debris traps were set at 2 downstream manholes. Crews vacuumed and jetted the main lines from manhole 1109G to 1109F and 1109E, no more debris was found in the system. Crews washed down street and vacuumed flow with combination truck. Water hydrant was flushed for 5 minutes. Crews set the combination truck at the Del Obispo street diversion gate valve site and vacuumed 1000 gallons for preventative measures. | N | Y | N | n/a | n/a | Storm drain - flushed and recovered | Y | N | N | n/a | 0
45001 | Charles Cheng (Voice) | 2004-08-03 21:03 | Mike Shope | (760)725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2004-08-03 18:30 | 2004-08-03 19:15 | 46.6 | 2100 | 1900 | 200 | Armory, Building 22213 | MCB CAMP PENDLETON | 92055-5008 | SD | Manhole 3-Y-303: VCP Line Size: 8 | 0 | 0 | Blockage | Roots and rock debris in the sewage collection system caused sewage to back up in the line and overflow the manhole (3-Y-303). | Ram jetted the line to clear blockage. A vacuum truck was used to recover most of the spilled sewage. The area was outlined with caution tape and warning signs were posted. Lime used to disinfect. FMD will continue preventative maintenance of the system.. | N | N | N | None | None | Overflow did not reach actual receiving waters but: Pooled on grassy area near manhole. | Y | Y | Y | Six signs were posted in the impacted area. | 3 | Remarks: Spill flowed from the manhole, traveling a maximum of 50 feet southwest, and pooled on a grassy area around the manhole. 1900 gallons were recovered. Total distance traveled: 50 feet. Expected public contact: Yes
045001 | Voice Mail | 07/13/04 0000 | Rich Arrant | (760) 744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-07-12 21:15 | 2004-07-12 22:40 | 2 | 170 | 0 | 170 | Woods Dr. | San Marcos | 92069 | SD | MH2747 | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | N | N | None | None | Soaked into Grass at MH | Y | N | Y | Area around MH | 3 | None
045002 | David Hanson | 2004-09-07 10:55 | Rich Arrant | (760)744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-09-06 12:43 | 2004-09-06 12:50 | 14 | 100 | 0 | 100 | Daisy LN. | San Marcos | 92069 | SD | MH1482 | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | N | N | None | None | Soaked intoground | Y | N | N | N/A | 0 | None
045003 | David Hanson | 2004-09-29 09:37 | Rich Arrant | (760)744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-09-29 08:40 | 2004-09-29 09:13 | 50 | 1650 | 1650 | 0 | Knoll Rd. | San Marcos | 92069 | SD | Private C/O | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | Y | N | None | None | Storm Drain | Y | Y | N | N/A | 0 | Recovered and Pumped into sewer
0405001 | David Hanson, fax (858) 467-2952 | 2004-07-24 12:15 | Brandon | (619) 892-9033 | U.S. Navy Public Works | Lincoln Property | 2004-07-24 12:15 | 2004-07-24 13:30 | 5 | 50 | 50 | 0 | NAB, Sewer lift station "B", Hwy 75 Silver Strand | Coronado | 92135 | SD | Lift Station | 0 | N/A | Pump Station Failure | Sewage discharged through possible loss of suction. Regained suction and tested system several times. | Regained suction and tested system several times. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | This spill was not from a PWC owned sewer line and should not be counted against PWC Utilities spill record. Site is operated by Lincoln Properties as a privatized utility system.
0405002 | David Hanson, fax (858) 467-2952 | 2004-08-02 08:30 | Christina Graulua | 619-545-8433 | U.S. Navy Public Works | U.S. Navy Public Works | 2004-08-03 21:57 | 2004-08-03 23:45 | 1 | 1670 | 1570 | 100 | NASNI, Kilo Pier | Coronado | 92135 | SD | Pump Station | 0 | N/A | POWER FAILURE | Lost power to pump staton and sewage from ship overflowed onto the pier | Investigating if emergency generator for pump station is warranted. | N | Y | Y | SD Bay | SD Bay | SD Bay | Y | Y | N | N/A | N/A | Noticed toilet paper on pier so did not witness the oveflow while it was occurring.
0405003 | David Hanson, fax (858) 467-2952 | 2004-08-04 | USS Ronald Regan | 619-556-7349 | U.S. Navy Public Works | U.S. Navy Public Works | 2004-08-04 01:15 | 2004-08-04 01:30 | 50 | 2350 | 1550 | 800 | NASNI, Kilo Pier | Coronado | 92135 | SD | Pump Station | 1 | N/A | POWER FAILURE | Lost power to pump staton and sewage from ship overflowed onto the pier | Re worked the electrical substation that was failing causing no power to the pump station. | N | Y | Y | SD Bay | SD Bay | SD Bay | Y | Y | N | N/A | N/A | Found a bad power substation and have repaired it.
0405004 | David Hanson, fax (858) 467-2952 | 2004-08-08 22:00 | Steve Rilatt | N/A | U.S. Navy Public Works | U.S. Navy Public Works | 2004-08-08 22:00 | 2004-08-08 22:30 | 8 | 250 | 0 | 250 | NAB housing Rendova Circle, Lift Station Failure | Coronado | 92135 | SD | Lift Station | 0 | N/A | Pump Station Failure | Pump station tripped off line. SCADA alarm alerted PWC who investigated. | Transducer found to have failed causing overheating of pumps and making them trip off line. | N | Y | N | N/A | N/A | Wooded area | N | N | N | N/A | N/A | Storm drain dumps onto a wooded area. Sewage infiltrated into the soil. Area was cleaned up as per PWC sewer spill cleanup SOP.
0405005 | David Hanson, fax (858) 467-2952 | 9/2/2004 14:00:00 pM | Leonard Dinson | 619-556-7352 | U.S. Navy Public Works | U.S. Navy Public Works | 2004-09-02 14:00 | 2004-09-02 16:00 | 2 | 250 | 0 | 250 | Point Loma Monument road | SD | 92106 | SD | Blockage | 0 | N/A | Blockage | Line serving Cabrillo National monument had a blockage causing sewer spill. | Hydroblasted line clear. | N | N | N | N/A | N/A | Point Loma Canyon, Bayside | Y | N | N | N/A | N/A | Overflow went into a canyon.
0405006 | David Hanson, fax (858) 467-2952 | 2004-09-15 15:30 | Matt Nadaeu | 619-805-5853 | U.S. Navy Public Works | U.S. Navy Public Works | 2004-09-14 15:30 | 2004-09-15 15:45 | 5 | 75 | 0 | 75 | NAB, Trident Way | Coronado | 92135 | SD | Blockage | 0 | N/A | Blockage | Lateral was blocked causing voerflow | Cleaned Lateral clear | N | Y | N | N/A | N/A | Stayed in storm drain catch basin and on pavement. Both were cleaned out by PWC. | Y | Y | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405007 | David Hanson, fax (858) 467-2952 | 09/27/2004 0805 | USS Ronald Regan | 619-545-1108 | U.S. Navy Public Works | U.S. Navy Public Works | 2004-09-27 08:05 | 2004-09-27 | 1 | 10 | 10 | 0 | NASNI, Kilo Pier | Coronado | 92135 | SD | Pump Station | 1 | 2004-08-04 | POWER FAILURE | Lost power to pump staton and sewage from ship overflowed onto the pier | Electrician investigating pump station and substation. | n | n | n | N/A | N/A | spill stayed on top of pier and was cleaned and sanitized by PWC | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
045004 | 1(858) 571-6972 | 2004-10-21 12:50 | Brian Walther | (619) 397-6042 | City of Chula Vista | City of Chula Vista | 10/21/04 1035 | 10/21/04 1035 | 100 | 50 | 40 | 10 | 890 G St. | Chula Vista | 91910 | SD | G St. Pump Station # 002 Public | None | N/A | LINE BREAK | While testing portable back-up pump check valve broke causing sewage to spray on paved area. This caused an assumed 50 gallons maximum to be discharged on paved area where most pooled on the uneven pavement. An estimated 10 and no more than 20 gallons were spilled into storm drain. | Pump was shut off immediately and combination trunk was dispatched to site to wash down and recover the contaminated area. Parts(Replacement check valve and necessary fittings) were ordered for replacemment of damaged equipment. | Yes | Yes | Yes | Storm drain north west corner of BF Goodrich Aerospace | San Diego Bay | N/A | Yes | N/A | N | N/A | N/A | Will procure and store mats to gag storm drain access in event of future spill.
045005 | 1(858) 571-6972 | 2004-10-30 11:00 | Mark W. Sanchez | (619) 397-6025 | City of Chula Vista | City of Chula Vista | 2004-10-29 16:30 | 2004-10-29 19:30 | 10 | 1800 | 1000 | 800 | 4344 Bonita Road | Chula Vista | 91902 | SD | WW Main Link # 155 Public | None | N/A | GREASE | Grease plugged 8'' sewer main | Broke plug with hydro flushed went through and hydro flusher back to where spill occurred. | Yes | Yes | No | None | None | Storm drain on Bonita Road | Yes | Yes | N | N/A | N/A | Sewage that reached storm drain basin was held up by debris and recovered by vacuum truck.
045006 | 1(858) 571-6972 | 2004-11-30 14:00 | Mark W. Sanchez | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 11/30/04 1345 | 11/30/04 1445 | 0.5 | 30 | 30 | 0 | 385 Parkway | Chula Vista | 91911 | SD | Private Sewer Cleanout | None | N/A | ROOTS | Roots in sewer lateral | Rodded out line, will film line repair if necessary | No | No | No | N/A | N/A | Parking lot of Parkway gym | No | No | N | N/A | N/A | BMP's set up in parking lot, sewer spill contained 100 percent. Area washed down and vacuumed up.
045007 | 1(858) 571-6972 | 2004-11-30 09:00 | Sierra Park Apartments | (619) 422-3788 | City of Chula Vista | City of Chula Vista | 11/30/04 0900 | 11/30/04 0930 | 2 | 60 | 50 | 10 | 827 Colorado Ave. | Chula Vista | 91911 | SD | N/A Private | None | N/A | PRIVATE PROPERTY | We removed a plastic toy figure | Cleared private sewer lateral stoppage with hand rods. We removed a plastic toy. We also televised the sewer lateral and washed down and vacuumed up 50 yards of gutter. The sewer lateral was in good condition, just a little grease. | Yes | Yes | No | None | None | Storm drain pipe | No | N/A | N | N/A | N/A | City was notified of private sewer lateral stoppage at 9:00 AM. We cleared stoppage at approximately 9:30 AM. We also cleaned up a small spill. | x
045008 | 1(858) 571-6972 | 2004-12-06 09:30 | Harry Gause (Apartment manager) | (619) 429-1208 | City of Chula Vista | City of Chula Vista | 12/6/04 0930 | 12/6/04 1030 | 1 | 60 | 0 | 60 | 778 Dorothy St. | Chula Vista | 91911 | SD | 119229 Private | None | N/A | GREASE | Grease | Cleared sewer blockage using Vactor Sewer Flusher. Advised manager to schedule a bimonthly flushing program or a grease control program. | Yes | Yes | No | None | None | Contained in unlined storm drain channel | No | N/A | N | N/A | N/A | City was notified at 9:30 AM cleared blockage at 10:30 AM.
045009 | 1(858) 571-6972 | 2004-12-15 19:30 | Chula Vista Police Department | (619) 619-5151 | City of Chula Vista | City of Chula Vista | 12/15/04 1400 | 12/15/04 2245 | 20 | 7935 | 135 | 7800 | 651 Palomar St. | Chula Vista | 91911 | SD | Private Sewer Main | None | N/A | PRIVATE PROPERTY | Private property sewer main stoppage, manager stated that problem started at 2:00 PM a plumber (Drain Patrol) was called. The plumber got his cable stuck in the main and could not clear the stoppage. The city was made aware of this problem at 7:30 PM. Spill was running into a private storm drain. | The city arrived on site at 8:00 PM. We started containment and put down BMP. Another plumber was called and a clean up company was also called. We stayed on site until the spilled had stopped. We left our BMP in place for clean up crew and the other plumber to use. | No | Yes | No | N/A | N/A | Unlined storm drain | Yes | Yes | N | N/A | N/A | We are not sure the amount of spill we are estimating is high enough because of peak usage hours. | x
045006 | Fax 619-338-2174 | 2004-11-29 11:54 | Guerrero, J | 619-522-7380 | City of Coronado | City of Coronado | 2004-11-29 08:00 | 2004-11-29 09:25 |  | 10 | 10 | 0 | 1108 Second Street | Coronado | 92118 | SD | Sewer Lateral | 1 | 2004-09-27 | PRIVATE PROPERTY | Blockage in private lateral | Plumber snaked line and cleared blockage. WWO crew contained and vacuumed up overflow | Y | N | N | N/A | N/A |  | Y | N | N | N/A |  |  | x
045007 | Fax 619-338-2174 | 2004-12-07 07:30 | LeMoine, K | 619-522-7380 | City of Coronado | City of Coronado | 2004-12-06 07:00 | 2004-12-06 15:30 |  |  |  |  | 814 Fourth Street | Coronado | 92118 | SD | Water line | 0 |  | OTHER | Private water line break | Potable water diverted to the sanitary sewer system | Y | N | N | N/A | N/A |  | Y | N | N | N/A |  | Courtesy notification only
045008 | Fax 619-338-2174 | 2004-12-11 13:00 | Guerrero, J | 619-522-7380 | City of Coronado | City of Coronado | 2004-12-11 11:40 | 2004-12-11 13:00 |  | 7 | 7 | 0 | 300 blk Orange/C alley | Coronado | 92118 | SD | Sewer Main | 1 | 2004-09-13 | GREASE | Roots, grease in sewer main line | Jetted and vacuumed line, rodded sewer main for roots | N | N | N | N/A | N/A |  | Y | N | N | N/A
045009 | Fax 858-694-3670 | 2004-12-13 17:00 | McGrath, J | 619-522-7380 | City of Coronado | City of Coronado | 2004-12-13 16:00 | 2004-12-13 17:00 |  | 5 | 5 | 0 | 900 blk Orange/D alley | Coronado | 92118 | SD | N/A | 0 |  | VANDALISM | Individual dumped can of gas in alley | Used vactor truck to remove puddle of gas | N | N | N | N/A | N/A |  | Y | N | N | N/A |  | Courtesy notification only
045003 | Quarterly Report | 2004-11-23 07:50 | Kip Curry | (858) 755-3294 | City of Del Mar | City of Del Mar | 2004-11-23 07:50 | 2004-11-23 08:00 | 1 | 10 | 10 | 0 | 1997 Zapo Street | Del Mar | 92014 | SD | Private lateral blockage at 1997 Zapo Street | 0 | N/A | BLOCKAGE | Private lateral blockage with overflow at clean out | Immediately installed cap on private lateral clean out. Told homeowner to stop using water and directed owner to have line repaired, which he did. City crews flushed and cleaned area. No further discharge from lateral. | N | N | N | none | none | Fully contained and recovered | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at 1997 Zapo Street.
045004 | Quarterly Report | 2004-11-29 17:00 | Resident of 704 Kalamath | (858) 755-3295 | City of Del Mar | City of Del Mar | 11/29/2004 N/A | 11/29/2004 N/A | N/A | N/A | N/A | 0 | 704 Kalamath | Del Mar | 92014 | SD | Private lateral stoppage at 704 Kalamath | 0 | N/A | BLOCKAGE | Private lateral blockage in resident's system | Per Standard Operating Procedures: rodded main line past resident's connection. No problem in City's system, small cut roots from resident's lateral cleared system. Conversation with resident, he rodded his own lateral and cleared stoppage. | N | N | N | none | none | City Sewer Main | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at 704 Kalamath.
045005 | Quarterly Report | 2004-12-03 21:30 | Rancho Dispatch, JPA | (858) 756-1126 | City of Del Mar | City of Del Mar | 2004-12-03 17:30 | 2004-12-03 23:12 | N/A | N/A | N/A | 0 | 1555 Camino Del Mar | Del Mar | 92014 | SD | Private lateral blockage in lower parking garage of Shopping Center "Del Mar Plaza" at 1555 Camino Del Mar | 0 | N/A | GREASE | Grease in private lateral is source of backup and overflow in private underground parking garage | Rodded main from Manhole B7-14 to B7-27 99' East, both runs with 4" auger. Maintenance of Plaza private lateral sewer system to be revised and lateral maintenance to be aggressively pursued by Plaza personnel. | N | N | N | none | none | City Sewer Main | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at 1555 Camino Del Mar
045006 | Quarterly Report | 2004-12-07 15:40 | Joyce Sharp | (858) 481-8483 | City of Del Mar | City of Del Mar | 12/7/2004 N/A | 2004-12-07 16:10 | N/A | N/A | N/A | 0 | 2435 Camino Del Mar | Del Mar | 92014 | SD | Private lateral blockage caused overflow in private residence | 0 | N/A | BLOCKAGE | Private lateral blockage caused overflow in private residence | Preventatively jet rodded City main approx. 75' north from A4-25 to A4-06. Line was clear, was fully jet rodded in November '04 | N | N | N | none | none | Interior overflow of residence, clean up will be done by homeowner. Final destination to City sewer system | Y | N | N | N/A | 0 | MAINTENANCE OF LATERALS ARE RESIDENTS RESPONSIBILITY, PER CITY ORDINANCE No 472 (02/02/87), Chapter 22.08.070 Private residential sewer lateral overflow at 2435 Camino Del Mar | x
045002 | David Hanson | 2004-11-12 08:30 | Kevin Wright | (619) 441-1658 | City of El Cajon | City of El Cajon | 2004-11-10 17:00 | 2004-11-10 18:30 | 1 | 90 | 0 | 90 | Estes St. | El Cajon | 92020 | SD | 15-123 | 0 | NA | GREASE | Accumulation of grease in line | Line was flushed (MH#15-124 to MH#15-123) and will be observed for possible inclusion in trouble spot list | Y | Y | Y | County Ditch | None | NA | Y | N | N | NA | 0 | County Ditch is completely fenced in, no public access
045003 | David Hanson 858-571-2724 | 11/17/04 0715 | Manuel Casas | (619)628-1372 | City of Imperial Beach | City of Imperial Beach | 11/17/04 0715 | 11/17/04 0745 | 25 | 750 | 725 | 25 | 7th & Basswood | City of Imperial Beach | 91932 | SD | Manhole #197 | 1 | 2003-12-16 | GREASE | There was a grease line build up between m/h #208 & M/H #219 that caused a partial blockage. | The Vactor truck was used to alleviate the blockage. The spill site was cleaned. Two Vactor truck loads (two thousand gallons) were vacuumed from the storm drain. The entire set of lines were cleaned from start to Pump Station #10. | N | Y | Y | San Diego Bay Wildlife Refuge | San Diego Bay | N/A | Y | N | N | N/A | 0 | The Vactor crew had been working on this area of town the day prior and would have hydraulically cleaned this line with in the next few days. The spill recovery was influenced by the water level at the outfall. The pond level is high enough that the outfall was submerged. The decision to vacuum out two thousand gallons was based on a more than doubling of the amount of gallons spilled. As the outfall was submerged, mathematical calculations of pipe capacity and logical estimating were used to determine the amounts recovered.
045004 | Quarterly Report | 11/20/04 1300 | Sheriff Department | (619)498-2400 | City of Imperial Beach | City of Imperial Beach | 11/20/04 1300 | 11/20/04 1345 | 0.25 | 12 | 12 | 0 | Donax and Florida | City of Imperial Beach | 91932 | SD | Manhole#679 | 0 | None | BLOCKAGE | There was a partial blockage in a very short line that self relieved prior to the Vactor truck showing up. | The Vactor truck was deployed to clear the line and clean the spill site. The effluent did enter the storm drain, so the downstream three storm drain lines were cleaned. The line was cleaned again the following workday. | N | Y | N | N/A | N/A | Vactor to Sewer | N | N | N | N/A | 0 | None
045005 | David Hanson 858-571-2724 | 12/03/04 1145 | A.J Moeller | (619) 628-1372 | City of Imperial Beach | City of Imperial Beach | 11/03/04 1100 | 11/03/04 1205 | 0.5 | 30 | 25 | 5 | 550 HWY 75 | City of Imperial Beach | 91932 | SD | Cleanout #154A | 0 | None | BLOCKAGE | This was a partial blockage in a line servicing a hotel with three guests. | The downstream lines were cleaned as a precaution due to the dark debris cleaned out of the partially blocked line. | N | Y | Y | Pond 10A | None | Pond 10A | Y | N | N | N/A | 0 | It was recently found out that this is a ponding system used to make salt. Additionally, it is a wildlife preserve and is not subject to public use. The pond level is raised and lowered by a series of gates with the intention of draining Pond 20 for salt reclamation.
045006 | David Hanson 858-571-2724 | 12/24/2004 1630 | Lifeguards | (619)423-0208 | City of Imperial Beach | City of Imperial Beach | 12/24/04 1630 | 12/24/04 1700 | 1 | 25 | 0 | 25 | I.B. Pier Restroom | City of Imperial Beach | 91932 | SD | I.B. Pier Restroom | 1 | 2004-08-29 | BLOCKAGE | The lateral was spilling intermittently. The cause of the blockage unknown. | The lifeguards noticed drips from a clean out under the pier. The lifeguards called the sewer emergency pager and the sewer duty man ordered the restroom, restaurant and lifeguard tower restroom to be closed. The sewer crew used a Vactor truck to attempt to clear the blockage and were unsuccessful. A plumber was called and a smaller trailer jetter was used to alleviate the blockage. The spill occurred over the Pacific Ocean, so there was no way to recover the sewerage. | N | N | Y | Pacific Ocean | N/A | Pacific Ocean | Y | N | N | N/A | 0 | None
045007 | David Hanson 858-571-2724 | 12/27/04 1045 | Lifeguards | (619)423-0208 | City of Imperial Beach | City of Imperial Beach | 12/27/04 1030 | 12/27/04 1145 | 1 | 75 | 0 | 75 | I.B. Pier Restroom | City of Imperial Beach | 91932 | SD | I.B. Pier Restroom | 2 | 8/29/2004 & 12/24/04 | BLOCKAGE | The lateral was spilling intermittently. The cause of the blockage unknown. | The lifeguards noticed the drips from the clean out on the pier. The lifeguards called the sewer duty pager and the sewer duty man ordered the pier restroom, restaurant and lifeguard tower restroom closed. A plumber was called and a small trailer jetter was unable to alleviate the blockage. The city crew used a city trailer jetter to clear the blockage. The spill occurred over the pacific Ocean so there was no way to recover the sewerage. | N | N | Y | Pacific Ocean | N/A | Pacific Ocean | Y | N | Y | 50' North and South of Pier | 3 | None
045009 | Quarterly Report | 12/26/2004 1230 | Sheriff Department | (619)498-2400 | City of Imperial Beach | City of Imperial Beach | 12/26/2004 1215 | 12/26/2004 1315 | 1 | 20 | 20 | 0 | 955 I.B. BLVD | City of Imperial Beach | 91932 | SD | Lateral | 0 | None | PRIVATE PROPERTY | The lateral was spilling intermittently. The cause of the blockage unknown. | The sewer crew directed the property owners to stop using water and call a plumber. Vactor cleaned from the spill site to the storm drain. Underground storm drain cleaned from F-33 to F-25. | N | Y | N | None | none | N/A | N | N | N | N/A | 0 | This is a private property lateral. | x
05-02 | FAX | 10-27-04 | Steven Maurer | 619-667-1488 | City of La Mesa | City of La Mesa | 10/27/2004 0945 | 10/27/2004 1200 | 5 | 675 | 0 | 675 | 8881 Fletcher Pkwy | La Mesa | 91942 | SD | 8" | 0 | N/A | INFILTRATION | Heavy Rains | Cleaned line | y | y | y | Alvarado Channel | San Diego River |  | Y | Y | N
045004 | 1(858) 571-6972 | 2004-10-21 12:50 | Brian Walther | (619) 397-6042 | City of Chula Vista | City of Chula Vista | 10/21/2004 1035 | 10/21/2004 1035 | 100 | 50 | 40 | 10 | 890 G St. | Chula Vista | 91910 | SD | G St. Pump Station # 002 | None | N/A | LINE BREAK | While testing portable back-up pump check valve broke causing sewage to spray on paved area. This caused an assumed 50 gallons maximum to be discharged on paved area where most pooled on the uneven pavement. An estimated 10 and no more than 20 gallons were spilled into storm drain. | Pump was shut off immediately and combination trunk was dispatched to site to wash down and recover the contaminated area. Parts(Replacement check valve and necessary fittings) were ordered for replacemment of damaged equipment. | Yes | Yes | Yes | Storm drain north west corner of BF Goodrich Aerospace | San Diego Bay | N/A | Yes | N/A | N | N/A | N/A | Will procure and store mats to gag storm drain access in event of future spill.
045005 | 1(858) 571-6972 | 2004-10-30 11:00 | Mark W. Sanchez | (619) 397-6025 | City of Chula Vista | City of Chula Vista | 10/29/2004 1630 | 10/29/2004 1930 | 10 | 1800 | 1000 | 800 | 4344 Bonita Road | Chula Vista | 91902 | SD | WW Main Link # 155 | None | N/A | GREASE | Grease plugged 8'' sewer main | Broke plug with hydro flushed went through and hydro flusher back to where spill occurred. | Yes | Yes | No | None | None | Storm drain on Bonita Road | Yes | Yes | N | N/A | N/A | Sewage that reached storm drain basin was held up by debris and recovered by vacuum truck.
045006 | 1(858) 571-6972 | 2004-11-30 14:00 | Mark W. Sanchez | (619) 397-6000 | City of Chula Vista | City of Chula Vista | 11/30/2004 1345 | 11/30/2004 1445 | 0.5 | 30 | 30 | 0 | 385 Parkway | Chula Vista | 91911 | SD | Sewer Cleanout | None | N/A | ROOTS | Roots in sewer lateral | Rodded out line, will film line repair if necessary | No | No | No | N/A | N/A | Parking lot of Parkway gym | No | No | N | N/A | N/A | BMP's set up in parking lot, sewer spill contained 100 percent. Area washed down and vacuumed up.
045007 | 1(858) 571-6972 | 2004-11-30 09:00 | Sierra Park Apartments | (619) 422-3788 | City of Chula Vista | City of Chula Vista | 11/30/2004 0900 | 11/30/2004 0930 | 2 | 60 | 50 | 10 | 827 Colorado Ave. | Chula Vista | 91911 | SD | N/A | None | N/A | PRIVATE PROPERTY | We removed a plastic toy figure | Cleared private sewer lateral stoppage with hand rods. We removed a plastic toy. We also televised the sewer lateral and washed down and vacuumed up 50 yards of gutter. The sewer lateral was in good condition, just a little grease. | Yes | Yes | No | None | None | Storm drain pipe | No | N/A | N | N/A | N/A | City was notified of private sewer lateral stoppage at 9:00 AM. We cleared stoppage at approximately 9:30 AM. We also cleaned up a small spill. | x
045008 | 1(858) 571-6972 | 2004-12-06 09:30 | Harry Gause (Apartment manager) | (619) 429-1208 | City of Chula Vista | City of Chula Vista | 12/6/2004 0930 | 12/6/2004 1030 | 1 | 60 | 0 | 60 | 778 Dorothy St. | Chula Vista | 91911 | SD | 119229 | None | N/A | GREASE | Grease | Cleared sewer blockage using Vactor Sewer Flusher. Advised manager to schedule a bimonthly flushing program or a grease control program. | Yes | Yes | No | None | None | Contained in unlined storm drain channel | No | N/A | N | N/A | N/A | City was notified at 9:30 AM cleared blockage at 10:30 AM.
045009 | 1(858) 571-6972 | 2004-12-15 19:30 | Chula Vista Police Department | (619) 619-5151 | City of Chula Vista | City of Chula Vista | 12/15/2004 1400 | 12/15/2004 2245 | 20 | 7935 | 135 | 7800 | 651 Palomar St. | Chula Vista | 91911 | SD | Private Sewer Main | None | N/A | PRIVATE PROPERTY | Private property sewer main stoppage, manager stated that problem started at 2:00 PM a plumber (Drain Patrol) was called. The plumber got his cable stuck in the main and could not clear the stoppage. The city was made aware of this problem at 7:30 PM. Spill was running into a private storm drain. | The city arrived on site at 8:00 PM. We started containment and put down BMP. Another plumber was called and a clean up company was also called. We stayed on site until the spilled had stopped. We left our BMP in place for clean up crew and the other plumber to use. | No | Yes | No | N/A | N/A | Unlined storm drain | Yes | Yes | N | N/A | N/A | We are not sure the amount of spill we are estimating is high enough because of peak usage hours. | x
045001 | Victor Vasquez, (858)571-6972 | 2004-09-16 16:30 | Greg Marquard | (949) 443-6367 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-09-11 09:55 | 2004-09-11 10:30 | 1 | 35 | 0 | 35 | 32012 Calle Delgado | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | GREASE | Grease was built up in main sewer line | Jetted mainline thoroughly; cctv videotaping of mainline; area put on priority maintenance schedule | N | Y | N | none | none | storm drain | Y | Y | N
045002 | FAX 858-571-6972 | 2004-12-08 10:00 | Michelle Perea | (949) 487-4315 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-12-07 15:55 | 2004-12-07 16:28 | 50 | 1600 | 0 | 1600 | Intersection of Ortega Hwy/Belford Dr | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | ROOTS | Roots in sewer line caused grease to build up, which in turn, caused the overflow. | City Contractor removed obstruction of roots and jetted the line several times. Sewer line will be cleaned in Feb/March 2005. | Y | Y | Y | San Juan Creek | Pacific Ocean | Pacific Ocean | Y | Y | N
045003 | Quarterly Report | Quarterly Report | Phil Falzarano | (949) 443-6396 | City of San Juan Capistrano | City of San Juan Capistrano | 2004-10-19 08:30 | 2004-10-19 10:00 | 8.8 | 792 | 0 | 792 | Via Cristal | San Juan Capistrano | 92675 | OC | Manhole | 0 | 0 | CONSTRUCTION | Rocks and debris in mainline blocking flow, which appears to be due to construction debris. | Jetted mainline before and after blockage; cctv videotaping of mainline; | Y | Y | Y | San Juan Creek | Pacific Ocean | San Juan Creek | N | N | N
004001 | fax | 10/01/2004 10:20 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 10/01/2004 09:00 | 10/01/2004 09:05 | 50 | 300 | 100 | 200 | North Coast Highway (101) at Avenida Encinas | Carlsbad | 92009 | SD | Air Vac # B3-AV-030 | 0 | N/A | Other | Air Vacuum release device drain valve left in open position | Removed drain valve handle, installed plugs | N | N | N | None | None | Percolated into soil | Y | N | N | N/A | N/A | DEHS determined spill did not require posting.
004002 | fax | 2004-10-20 18:30 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2004-10-20 10:22 | 2004-10-20 10:37 | 200 | 3000 | 0 | 3000 | Alga Road at Almaden Lane | Carlsbad | 92009 | SD | Unaccepted manole on Nside of Alga Rd | 0 | N/A | Construction | Debris and mud from construction site drained into public sewer | Installed concrete plug (bulkhead) in line from construction site | Y | Y | Y | San Marcos Creek | Pacific Ocean | Pacific Ocean, South Carlsbad Beach | Y | Y | Y | So. Carlsbad Beach | 3 | Developer required to prevent flow into public sewer prior to final acceptance. Pursuing claims on behalf of impacted homeowners. OES#04-05474
034005 | voice mail @ (858)467-2952 | 2004-11-11 14:00 | Alice Benson | 760-789-1330 | Ramona Municipal Water District | Ramona Municipal Water District | 2004-11-10 16:00 | 2004-11-11 08:00 | 400 | 379200 | 0 | 379200 | 24157 San Vicente Road | Ramona | 92065 | sd | recycled water pipe line | 0 | 0 | LINE BREAK | 6" pipe broke inside golf course | repaired line, new procedures in place to monitor | Y | n | y | san vicente creek | san vicente resevoir | san vicente resevoir | y | y | N | n/a |  | OES control # 04-5910 spill was recycled water
45002 | FAX | 2004-12-12 17:15 | JOHN PASTORE | (760) 479-4121 | Rancho Santa Fe Community Services District | Rancho Santa Fe Community Services District | 12/12/04 1015 | 12/12/04 1045 | 30 | 900 | 900 | 0 | El Camino Real & La Orilla | Rancho Santa Fe | 92067 | SD | ECRFM-01 | 1 | 2004-09-25 | LINE BREAK | Traffic accident - A vehicle left the road and hit the guardrail and then struck our sewer air-vacuum device on the forcemain. The air-vac device piping was severed. | We will install larger and stronger pipe guards to protect the structure. | N | N | Y | Drainage creek at El Camino Real and La Orilla. | None | Recovered and trucked to the sewer treatment plant for disposal. | Y | Y | N | None | NA | The area of contamination was isolated and 4000 gallons of standing water was vactored out and recovered for disposal at the sewer treatment plant.
045002 | FAX 858-571-6972 | 2004-12-13 11:35 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2004-12-12 09:50 | 2004-12-12 10:10 | 3 | 60 | 60 | 0 | 26752 Calle Almanza | Capistrano Beach | 92624 | OC | MANHOLE NO. 458 | 0 | NONE | ROOTS | District crew found a small amount of sewage flowing out of MH #458 pick holes. Crew removed a root mass of approx. 4" in diameter and 3" in length. Root mass of this size is indicative of private sewer lateral cleaning. | SCWD mainline in this area was last cleaned out on April 1, 2004. To try to determine exact origin of root mass, SCWD video crew inspected lines and sewer lateral connections from MH #457 to #459. Video crew found two sewer laterals impacted with roots at a connection to main. Homeowners have been notified with door hangers that their lateral needs to be cleaned due to root intrusion and they must contact SCWD prior to cleaning so that SCWD could respond by placing a debris trap downstream to prevent future sewer overlfows of this kind. | N | N | N | n/a | n/a | Street surface. | Y | N | N | n/a | 0
45002 | Charles Cheng (voice) | 10/06/04 13:52 | Mike Shope | (760) 725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 10/05/2004 11:00 | 10/05/2004 17:30 | 3.2 | 1250 | 0 | 1250 | Building 53426 | MCB CAMP PENDLETON | 92055-5008 | SD | Building lateral | 0 | N/A | ROOTS | Blockage of roots and baby wipes occurred in the main line causing the flow to backup and overflow the building lateral. | The line was cleared using a ram jetter. Sand bags were placed at the storm drain inlet to stop flow into the storm drain. Lime was used around building lateral to disinfect the area. FMD will continue preventative maintenance of the sewage lines. | N | Y | Y | None | None | Overflow did not reach actual receiving waters but: Dry ditch. | Y | Y | N | none | 0 | The spill traveled from a lateral over earthen area, then down sidewalk into a concrete-lined swale. The spill entered a storm drain inlet traveled under the road then exited the storm drain and discharged into a dry ditch.. Total distance 892 feet.
045001 | Voice Mail | 07/13/04 0000 | Rich Arrant | (760) 744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-07-12 21:15 | 2004-07-12 22:40 | 2 | 170 | 0 | 170 | Woods Dr. | San Marcos | 92069 | SD | MH2747 | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | N | N | None | None | Soaked into Grass at MH | Y | N | Y | Area around MH | 3 | None
045002 | David Hanson | 2004-09-07 10:55 | Rich Arrant | (760)744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-09-06 12:43 | 2004-09-06 12:50 | 14 | 100 | 0 | 100 | Daisy LN. | San Marcos | 92069 | SD | MH1482 | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | N | N | None | None | Soaked intoground | Y | N | N | N/A | 0 | None
045003 | David Hanson | 2004-09-29 09:37 | Rich Arrant | (760)744-0460 | Vallecitos Water District | Vallecitos Water District | 2004-09-29 08:40 | 2004-09-29 09:13 | 50 | 1650 | 1650 | 0 | Knoll Rd. | San Marcos | 92069 | SD | Private C/O | 0 | N/A | GREASE | Grease Blockage | Jetted and added to Fog treat List | N | Y | N | None | None | Storm Drain | Y | Y | N | N/A | 0 | Recovered and Pumped into sewer | x
045001 | VOICE MAIL Charles Chang | 2004-10-05 11:30 | Ted Eich | 951-674-3146 | Elsinore Valley Municipal Water District | Elsinore Valley Municipal Water District | 10/4/2004 2215 | 10/5/2004 0615 | 1.09 | 8777 | 1000 | 7777 | 32575 McVicar | Wildomar | 92595 | RV | Force Main | 0 | 0 | CONSTRUCTION | during construction, check valve removed and no brace installed. Flexible coupling slipped ouot of place. | Pipe pushed into position. Verified brace installed. | N | Y | N | none | none | storm channel | Y | Y | N | na | 0 | Flexible coupling was shown on plans. Contractor removed contaminated soil.
0405008 | David Hanson, fax (858) 467-2952 | 10/14/2004 0715 | Tim Couto | 619-553-4144 | U.S. Navy Public Works | U.S. Navy Public Works | 10/14/2004 0715 | 10/14/2004 0815 | 8.3 | 500 | 175 | 325 | SUBASE, BLDG 513, Ashburne Road | San Diego | 92152 | SD | Main | 0 | N/A | Roots | Bundle of roots blocke the 6" main | Removed all roots from upstream manholes; Spill contained in parking lot. | N | N | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405009 | David Hanson, fax (858) 467-2952 | 10/26/2004 1400 | Duty Desk Mr. Seke | 619-556-7349 | U.S. Navy Public Works | U.S. Navy Public Works | 10/26/2004 1400 | 10/26/2004 1420 | 0.5 | 10 | 10 | 0 | CORONADO, BLDG 204, Quay Road | San Diego | 92118 | SD | Line | 0 | N/A | Line Break | Small crack in 1" vent line | Vent line removed and plugged. | N | Y | N | N/A | N/A | N/A | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405010 | David Hanson, fax (858) 467-2952 | 10/29/2004 1841 | Chief Samaniego | 619-247-8897 | U.S. Navy Public Works | U.S. Navy Public Works | 10/29/2004 1835 | 10/29/2004 1836 | 10 | 10 | 0 | 10 | NAVAL STATION, Quay Wall Pier 7/8 | San Diego | 92132 | SD | Riser | 0 | N/A | OTHER | Bad connection from ship to shore connector | Re- connected | Y | N | Y | San Diego Bay | N/A | San Diego Bay | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405011 | David Hanson, fax (858) 467-2952 | 11/26/2004 1040 | Robert Witherington | 619-553-4144 | U.S. Navy Public Works | U.S. Navy Public Works | 11/26/2004 1040 | 11/26/2004 1130 | 0.1 | 35 | 35 | 0 | SUBASE, White Poao St. | San Diego | 92152 | SD | Pipe | 0 | N/A | Blockage | Line blocked due to solids clogging the line. | Line Hydroblasted | N | N | N | N/A | N/A | All wastewater collected by vacuum truck | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
045010 | 1(858) 571-6972 | 2005-02-16 10:00 | Orlando Monreal | (619) 585-7266 | City of Chula Vista | City of Chula Vista | 2/16/2005 0730 | 2/16/2005 1200 | One gallon per flush | 50 | 25 | 25 | 464 "H" St. | Chula Vista | 91910 | SD | N/A (Private clean out) | None | N/A | PRIVATE PROPERTY | Private sewer lateral blockage cause unknown | Store manager (Orlando Monreal) called Bill Howe Plumbing to clear blockage | No | Yes | Yes | City Storm Drain | "J" St. Bay Marina (San Diego Bay) | N/A | Yes | N/A | N | N/A | N/A | We received the call from citizen at 10:00 am. The containment of spill started at 10:30 am. We advised store manager to call plumber. We stayed on site for containment until plumber arrived and set up his containment. The store Express Tire Company opened at 7:30 am. There is only one bathroom in the building. | x
045011 | 1(858) 571-6972 | 2005-03-13 19:45 | Mark Sanchez | (619) 697-6000 | City of Chula Vista | City of Chula Vista | 2005-03-13 16:00 | 2005-03-13 19:00 | 5 | 1000 | 600 | 400 | 1337 Old Janal Ranch Rd. | Chula Vista | 91910 | SD | Sewer Manhole | One | 2004-11-02 | GREASE | Siphon in sewer main with net cover started to accumulate grease and debris over it, causing blockage and sewer overflow. | Flushed sewer line with Vactor, broke plug and vacuumed grease and debris from manhole, area not accepted by City of Chula Vista, referred problem to city inspectors. | No | Yes | Yes | Storm Drain Catch Basin | Salt Creek | Salt Creek | Yes | Yes | N | N/A | N/A | N/A
045112 | 1(858) 571-6972 | 2005-03-22 07:45 | Mark Sanchez | (619) 697-6000 | City of Chula Vista | City of Chula Vista | 3/21/2005 0925 | 3/21/2005 0945 | 5 | 100 | 100 | None | 1665 Brandywine Ave. | Chula Vista | 91910 | SD | Sewer Lateral | None | N/A | ROOTS | Heavy roots from apartment sewer lateral caused sewer to backup. Lateral rodded out by city crews, plug broken. Flow reached basin, but was help up by debris, 100% containment. | Line rodded out, stormwater complicance officer called out apartment complex told to set up maintenance program. | No | Yes | No | Storm Drain Catch Basin | N/A | Catch Basin | No | No | N | N/A | N/A | N/A
045007 | Quarterly Report | 2005-01-13 17:30 | Called in by resident David Arnold via North County Dispatch, JPA to Public Works on-duty personnel Sam Madrigal & Paul Thomas | (858) 755-3294 | City of Del Mar | City of Del Mar | 2005-01-13 17:30 | 2005-01-13 18:40 | 1 | 70 | 0 | 70 | Manhole C12-03 at 302 Ocean View Avenue | Del Mar | 92014 | SD | Manhole C12-03 at 302 Ocean View Avenue | 0 | N/A | ROOTS | Roots, grease and rags | Rodded main from Manhole B12-02 to Manhole C12-03 (Rodded twice with 4" auger) 2x 185', follow up 1/14/05 used jet rodder 2x200' | N | N | N | none | none | Anderson Cyn dirt absorbed | Y | N | N | N/A | 0 | None
045008 | Quarterly Report | 2005-03-20 10:38 | Called in by resident of 640 Amphitheatre Drive via North County Dispatch, JPA to Public Works on-duty personnel Sam Madrigal & Dan Peters | (858) 755-3294 | City of Del Mar | City of Del Mar | 2005-03-20 10:30 | 2005-03-20 11:30 | 0.66 | 40 | 40 | 0 | 640 Amphitheatre Drive | Del Mar | 92014 | SD | Resident's Lateral Clean Out at 640 Amphitheatre Drive | 0 | N/A | ROOTS | Heavy roots in main | Rodded main from Manhole C8-15 to Manhole C8-17 (Rodded twice with 2" and 4" auger) 2x 250' | N | N | N | none | none | Fully contained and recovered. | Y | N | N | N/A | 0 | On 11/29/2004 there was a Private lateral stoppage in resident's system at 704 Kalamath, which is within 1000' of current overflow location, but there was no overflow at that time (the event was reported in previous quarterly report No. 045004) | x
045010 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-01-12 08:05 | 2005-01-12 10:30 |  | 8 | 8 | 0 | 200 blk B/C alley | Coronado | 92118 | SD | Private lateral | 0 |  | PRIVATE PROPERTY | Cleanout cap broken, allowed sewage to leak into alley | City staff captured sewage, private contractor replaced sewer cleanout cap | Y | N | N | N/A | N/A | Vactored up | Y | N | N | N/A |  |  | x
045011 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-03-03 08:45 | 2005-03-03 10:45 | 0.416 | 50 | 50 | 0 | 301 Orange Avenue | Coronado | 92118 | SD | Sewer Main | 2 | 09/13/04, 12/11/04 | ROCKS | Rocks in sewer main line obstructed flow | Jetted line and vacuumed up debris. Repairs to City main line are scheduled when CalTrans permit obtained. | Y | N |  | N/A | N/A | Vactored up | Y | N | N | N/A
045010 | Quarterly Report | 1/05/05 1230 | Mavis Klute | (760)438-1658 | City of Imperial Beach | City of Imperial Beach | 1/05/05 1230 | 1/05/05 1300 | 1 | 20 | 20 | 0 | 194 Ebony Ave | City of Imperial Beach | 91932 | SD | Lateral | 0 | None | PRIVATE PROPERTY |  | The homeowners son was asked to stop the water usage at the property and to call a plumber. He was extremely cooperative and wanted to correct the problem immediately. The water had flowed onto the concrete alley and ran to the end of the block where the sewer supervisor put down absorbant materials to block the flow travel. The homeowner stated they would have the plumber clean the spill site and alley. When the sewer supervisor returned two hours later, the alley appeared to have been cleaned up. | Y | N | N | None | None | N/A | N | N | N | N/A | 0 | This is a private property lateral. | x
045011 | David Hanson 858-571-2724 | 1/17/05 1000 | I.B. Lifeguards | (619)423-0208 | City of Imperial Beach | City of Imperial Beach | 1/17/05 1000 | 1/17/05 1100 | 1 | 25 | 0 | 25 | I.B. Pier Restroom | City of Imperial Beach | 91932 | SD | I.B. Pier Restroom | 4 | 8/29/2004 & 12/24/04 & 12/27/04 & 1/1/05 | BLOCKAGE |  | The lifeguards noticed drips from a clean out under the pier. The Port of San Diego was notified and the Port Plumber (Pete Budda 619.929.2789) responded and snaked and then flushed the pier sewer line. The spill occurred over the Pacific Ocean, so there was no way to recover the sewerage. | N | N | Y | Pacific Ocean | N/A | N/A | Y | N | Y | 50' North and South of Pier | 3 | This is a Port of San Diego responsibility. The hard entry lines of responsible sewer agency in the RWQCB quarterly excel report forces the City of Imperial Beach to report Imperial Beach as responsible agency.
045012 | David Hanson 858-571-2724 | 1/18/05 1438 | I.B. Lifeguards | (619)423-0208 | City of Imperial Beach | City of Imperial Beach | 1/18/05 1438 | 1/18/05 1510 | 1 | 25 | 0 | 25 | I.B. Pier Restroom | City of Imperial Beach | 91932 | SD | I.B. Pier Restroom | 5 | 8/29/2004 & 12/24/04 & 12/27/04 & 1/1/05 & 1/17/05 | BLOCKAGE |  | The lifeguards noticed drips from a clean out under the pier. The Port of San Diego was notified and a contracted plumber SOS Plumbing came and jetted from the cleanout adjacent to the lifeguard tower 400' to the East and allieviated the blockage. The spill occurred over the Pacific Ocean, so there was no way to recover the sewerage. | N | N | Y | Pacific Ocean | N/A | N/A | Y | N | Y | 50' North and South of Pier | 3 | This is a Port of San Diego responsibility. The hard entry lines of responsible sewer agency in the RWQCB quarterly excel report forces the City of Imperial Beach to report Imperial Beach as responsible agency.
045003 | FAX to 858-467-2952 | 2005-01-12 17:00 | D Catone | (619) 825-3810 | City of Lemon Grove | City of Lemon Grove | 2005-01-10 08:30 | 2005-01-10 10:30 | 15 | 1800 | 900 | 850 | Lemon Grove Ave | Lemon Grove | 91945 | SD | 576-35-03 | 2 | 07/26/04 8/02/04 | UNKNOWN | Possible debris left over form major vandalism of 7-26-05 | Video taped. Found piece of clay pipe lodged at manhole. Estimated as part of repair made upstream 7/04 due to vandalism | Y | Y | Y | Chollas Creek | S D Bay | S D Bay | Y | N | N | none | 0 | Heavy rainfall preoceeding overflow. All ditches at full capacity.
045001 | Fax | 2004-08-23 10:00 | David Vigliotti | 858-668-4719 | City of Poway | City of Poway | 2004-08-20 08:00 | 2004-08-20 08:15 | 3 | 45 | 25 | 20 | 13608 Pomerado Rd | Poway | 92064 | SD | 6" private lateral | 0 |  | PRIVATE PROPERTY | Roots and possible separation on private side of sewer system was cause of discharge. Private 6" sewer cleanout is located approx. 20 ft from curb area. | Private cleanout was rodded and cleared; containment barriers in three locations were set up and spill vacuumed with Vactor. Storm drain pipes and two collection boxes were jet-rodded and Vactored as additional measure. Area downstream within concrete channel has limited public access; no signs posted. | N | Y | Y | Drop inlet on Pomerado Rd | Pomerado Channel |  | Y | N | N |  |  | Apartment complex manager was notified of sewer lateral damage on private side of system. Customer contacted private contractor while City crews on-site; area was being prepped for repairs when crews left. | x
045002 | Fax | 2005-01-31 14:30 | Roger Morrison | 858-668-4636 | City of Poway | City of Poway | 2005-01-31 11:30 | 2005-01-31 12:05 | 6 | 210 | 10 | 200 | Rios Rd/Pomerado Rd | San Diego | 92128 | SD | Manhole | 1 | 2004-06-10 | CONSTRUCTION | Inadequate communication between Construction Mgr and proper Public Wks personnel. To allow installation of new flow meter, Camino del Valle LS was temporarily shutdown. The LS was shutdown too long, causing the gravity sewer line that runs to the LS to backup into emergency overflow line that runs to the City of San Diego. San Diego line did not have the capacity to take add'l flow and it overflowed the manhole. | Improved communication, along with sufficient monitoring of sewage system will take place if another shutdown is necessary. Also, shutdowns will only be allowed during low-flow conditions. | Y | Y | Y | Unnamed stream | Lake Hodges |  | Y | N | N |  |  | Initial receiving waters: Unnamed stream in Thom Bros, page 1170, sectors C3, B2, etc.
045024 | faxed | 2005-01-10 15:40 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-01-09 11:00 | 2005-01-09 02:00 | 25 | 21000 | 21000 | 0 | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 0 | N/A | Flood damage | Infiltration due to heavy rain showers from heavy rain storm that hit the area | Raceway pump station will be soon replaced with a new pump station. The City of Vista sent out the bids for the new pump station. The bid opening for the pump station is March 25, 2005. | Y | N | N | None | None | Retention area around station compound | Y | N/A | Y | Perimeter of compound | Still posted | Raceway pump station is still under guarded condition with crews stationed at pump station 24-hours until storm passes. Also have pumper trucks running around the clock until storm passes.
045025 | faxed | 2005-01-12 07:45 | Richard Flynn | 760.726-1340 | City of Vista | City of Vista | 2005-01-11 15:16 | 2005-01-11 16:04 | 25 | 1200 | 700 | 500 | 455 Hillway Drive | Vista | 92083 | SD | V23 | 0 | N/A | Roots | Excessive amount of storm water and roots caused gravity flow sewer line to become blocked resulting in overflow and spill. | Preventive maintenance, CCTV survey and infiltration preventive practices and BMPs. | Y | Y | Y | Beaumont Easement Storm Channel | Buena Vista Creek |  | Y | N/A | Y | Beaumont School | Still posted | Due to heavy ground water saturation and heavy rain showers could not effectively capture 100%. Amount of stormwater flow was at flood stage at the time of spill, estimated flow of stormwater was at 50 GPM.
045026 | faxed | 2005-01-12 10:05 | Jim Gusman | 760.726-1340 | City of Vista | City of Vista | 2005-01-11 08:00 | 2005-01-11 08:10 | 100 | 2300 | 2300 | 0 | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 0 | N/A | Flood damage | Heavy rain | Work with Encina Wastewater Authority to bypass and ramp down Buena Pump Station to allow Vista to continue pumping into shared pressure main. Also brought in up to four pumper trucks to transfer flow to the Vista/Carlsbad interceptor trunk line | Y | N | N | None | None | Raceway Pump Station holding/containment area | Y | N | Y | Around pump station and containment area | Still posted | Wash down area with bleach today (01/12/05) capture and pump out containment area. OEM not notified because spill contained to pump station area.
045027 | faxed | 2005-02-21 19:29 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-02-21 10:20 | 2005-02-22 10:30 | 5 | Unknown | 200 | Unknown | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 2 | 2005-01-11 | Infiltration | Heavy, record breaking rain in county; inflow and infiltration | The new Raceway Pump Station will soon be built. Scheduled completion date is December 2005. | Y | N | Y | Aqua Hedionda Creek | None | Creek | Y | N | N | None - to dangerous to post at this time | N/A | Heavy rains filled our holding area causing some of the contamination runoff and sewage to hit the creek.
045028 | faxed | 2005-02-22 19:29 | George Solano | 760.726-1340 | City of Vista | City of Vista | 2005-02-22 07:37 | 2005-02-22 07:42 | 5 | 25 | 25 | None | 2689 S. Melrose Drive | Vista | 92083 | SD | Raceway Pump Station | 2 | 1/11/2005, 2/21/2005 | Infiltration | Heavy, record breaking rain in county; inflow and infiltration | City of Vista was at the pump station during one of the heavy rain events causing a small amount of sewage left the wet well. Crews adjusted accordingly and vacuumed up the spill. | Y | N | N | Holding area around pump station | None | Holding area around pump station | Y | N | N | None | N/A | Heavy rains came through our area causing small spill, approximately 25 gallons.
045029 | faxed | 2005-03-11 09:40 | Jim Gusman | 760.726-1340 | City of Vista | PRIVATE PROPERTY | Unknown | Unknown / Private | 1 | Unknown | 100 | Unknown | 1138 Cielita Linda | Vista | 92083 | SD | Private septic sewer system | N/A | N/A | Unknown | Unknown | Vacuumed and washed down right-of-way, sandbagged and bermed spill area and catch basin; notified storm drain enforcement officer. Sample tested, high fecal count, dye tested on 03/10/2005, no results as yet. Either from 1134 or 1138 Cielita Linda. | Unknown - none during response notification or on 03/09/2005 | Unknown | Unknown | None | None | N/A | Y | N | Y | 1138 Cielita Linda | N/A | Turned over to Mikhail Ogawa - 619.994.7074 | x
045030 | faxed | 2005-03-26 09:30 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE PROPERTY | 2005-03-26 06:00 | 2005-03-26 07:40 | 10 | 60 | 45 | 5 | 1244 N. Santa Fe Avenue | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | Contacted property management, no response. Followed up by calling ASAP Plumbing to clear drain along with Vista Irrigation District (Mark) to shut off water at complex to stop overflow. Overflow area was damned off (06:40) Vactor truck (Unit 527) was used to vacuum up overflow and washed down. | Y | Y | N | None | None | Storm drain at N. Santa Fe Avenue and W. Indian Rock Road | N | N | N | N/A | N/A | Plumber on scene at 07:25, Vista Irrigation District on scene at 07:40, water turned off at 07:50. | x
045031 | faxed | 2005-03-27 16:51 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE PROPERTY | 2005-03-27 11:54 | 2005-03-27 14:00 | 10 | 850 | 0 | None | 1333 Olive Avenue (Tiki Village Mobile Home Park) | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | All but 10 gallons were contained in space #26 bathrooms (2) and interior of house some sewer was under house and we were able to contain this small amount by damning it. Property owner had ASAP Plumbing Co. clear the line at 14:00 hrs. Gave property owner and manager copy of the City of Vista policy explaining owner responsibility. | Y | N | N | None | None | Private property in house. | N | N | N | N/A | N/A | All sewage was contained at space #26. Property owner was made aware of damage to space #26. | x
045032 | faxed | 2005-03-26 | Mike Teem | 760.726-1340 | City of Vista | PRIVATE PROPERTY | 2005-03-26 14:05 | 2005-03-26 17:00 | 3 | 540 | 500 | 40 | 1205 Monique Court, Units A - D | Vista | 92083 | SD | PRIVATE LATERAL | N/A | N/A | Unknown | Private lateral plugged. | Called out ASAP Plumbing Co. to clear blockage. Damned up flow and used Vactor #527 to vacuum up water and washed down area. Line cleared at 17:00. Resident advised to stop water usage at 16:30. | Y | N | N | None | None | Private property in house. | N | N | N | N/A | N/A | Was told by resident that this has been an on-going problem for approximately four (4) days; unable to determine exact duration at this time. | x
005001 | fax | 01/30/2005 16:05 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 01/30/2005 10:08 | 01/30/2005 10:48 | 20 | 800 | 0 | 800 | 6547 Avenida del Paraiso | Carlsbad | 92009 | SD | Meadows 1 Pump Station Force Main | 0 | N/A | pump station failure | 4 inch ACP force main developed leak, extent of pipe damage unknown due to 8' depth below grade | Excavate line, repaired force main leak | Y | Y | N | None | None | Percolated into soil | Y | N | N | N/A | N/A | DEHS determined spill did not require posting.
005002 | fax | 2005-02-15 10:00 | Leo Schempp | 760-753-0156 | Leucadia County Water District | Leucadia County Water District | 2005-02-15 09:15 | 2005-02-15 09:48 | 5 | 200 | 150 | 50 | 7683 Sequoia St. | Carlsbad | 92009 | SD | MH # 08-13970 | 0 | N/A | other | Miscommunication concerning bulkhead left in recently accepted sewer | District Engineer and Construction inspector implementing permit program for sewer bulkheads | Y | Y | Y | San Marcos Creek | Batiquitos Lagoon | NA | Y | N | N | N/A | N/A | LWD inspector conducting audit of all construction projects, veriying all bulkheads
005003 | fax | 2005-02-18 11:15 | Leo Schempp | 760-753-0157 | Leucadia County Water District | Leucadia County Water District | 2005-02-18 08:58 | 2005-02-18 09:10 | 60 | 720 | 0 | 720 | 7504 Gibraltar St. | Carlsbad | 92010 | SD | MH# 10-1870 | 0 | N/A | debris | Crew found grease and excessive grit | Flat main line cleaned quartly, CCTV inspected schedule changed to monthly | Y | Y | Y | San Marcos Creek | Batiquitos Lagoon | NA | Y | N | N | N/A | N/A | La Costa Golf course manager (Steve Aukland) advised of sewer spill, instructed to inform employees that sewagw is in creek
045001 | David Hanson | 2005-01-09 15:00 | Martin Holmes | 619 258-4706 | Padre Dam Municipal Water District | Padre Dam Municipal Water District | 2005-01-09 11:30 | 2005-01-09 13:30 | 275 | 33000 | 0 | 33000 | 9040 Carlton Oaks Dr | Santee | 92072 | SD | Manhole at Lake 2 | 1 | 2004-02-22 | INFILTRATION | Pump station unable to handle sewage surge of 1.3 mgd. | Locked down manhole lid, so sewage can surcharge back up our system to the treatment plant . | Y | N | Y | Santee Lake # 2 | Santee lLake 2 | Santee Lake 2 | Y | Y | Y | Around perimeter of Lakes 1 & 2 | 14 | Engineering working on new Concept for this manhole
045002 | voice mail @ (858)467-2952 | 01/20/05 11:47 | Ron Gunnett | 760-789-1330 | Ramona Municipal Water District | Ramona Municipal Water District | 2005-01-20 08:00 | 2005-01-20 18:00 | 3.5 | 1500 | 0 | 1500 | Vista Vincente Rd and Ct | Ramona | 92065 | SD | MH 120 | 0 | 0 | OTHER | SD Co storm failed, main broke | Isolate water, bypass, repair | Y | Y | N | Golf Course Pond | None | None | Y | N | N | n/a | 0 | None
045003 | FAX 858-571-6972 | 2005-01-03 12:45 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-01-03 11:45 | 2005-01-03 12:25 | 35 | 1400 | 75 | 1325 | 31871 Circle Drive | Laguna Beach | 92651 | OC | Clean out at sewer tunnel drop MH 1166 | 0 | NONE | BLOCKAGE | During a routine inspection by the District's lift station crew, the crew discovered wastewater flowing out of a manhole into an adjacent storm basin. The crew found a solid object blocking the sewer pipeline. After several attempts with the steel rod from a cleaning machine, the blockage was cleared and the normal flow resumed. | The source and type of blockage is unknown and since it was broken loose and forced into the larger 24" sewer pipe in the sewer tunnel, it was almost impossible to identify what the blockage was. These lines were recently cleaned in 11/04 as part of the SCWD's annual maintenance program and the video inspection indicates that all pipes and manholes are in good condition with no obstructions. There had been substantial rain and some localized flooding in the general upstream area of this SSO and it is possible that storm water run off was diverted into the SCWD sewer system manhole in this area by unknown parties. Debris from stormwater runoff could have entered the sewer line and caused the blockage. SCWD crews will install locking MH lids at MH 1154, 1092 and 1153 to prevent future SSO's of this type. | Y | Y | Y | Pacific Ocean | n/a | n/a | Y | Y | Y | Seacliff Drive to 1000 steps County Beach | 3
045004 | FAX 858-571-6972 | 2005-01-07 19:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 1//7/2005 19:30 | 2005-01-07 20:11 | 15 | 600 | 0 | 600 | 34281 Camino El Molino | Capistrano Beach | 92624 | OC | MH 331 | 0 | NONE | BLOCKAGE | Blockage in main line caused overflow at Manhole 331. Crews retrieved 2-1/2 gallons of debris and roots out of sewer line at Manhole 332. | Crews completed additional video and visual inspection from MH 330 to 331 to 333 and found all lines intact and free of any obstructions. It is suspected that a plumber pushed roots and debris into SCWD sewer main while maintaining a private lateral. SCWD is preparing to issue letters with photographs of root impacted laterals to homeowners requesting them to clean their laterals and notify SCWD prior to work so the District can collect roots and debris at downstream manhole to prevent further SSO's. This process will be implemented in phases and a pilot program is planned tentatively for March 2005 when the first 35 homewoners will be notified. | Y | Y | Y | Pacific Ocean | n/a | n/a | Y | N | Y | 35051 Beach Road - 100 yards from each side of strom drain discharge into ocean | 4
045005 | FAX 858-571-6972 | 2005-03-23 11:55 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-03-21 | 2005-03-23 08:30 |  | 30 | 30 | 0 | 34036 Amber Lantern | Dana Point | 92629 | OC | Lateral line | 0 | NONE | ROOTS | Property owner's sewer lateral was clogged with heavy root buildup beginning approximately one foot up from the sewer main. Cap removed from cleanout and sewage coming out of it. | After putting a debris trap downstream to catch roots, SCWD crews ran jetter in main line. SCWD crews retrieved roots in the main line that came from the service lateral cleaning. | N | N | N | n/a | n/a | Overflow saturated into the ground around the cleanout. | Y | N | N | n/a | 0 | Private System Overflow Incident | x
45003 | Charles Cheng (voice) | 2005-01-11 16:40 | Christine Ricafrente | (760) 725-9761 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2005-01-11 12:00 | 2005-01-11 15:00 | 30 | 5400 | 0 | 5400 | Building 630121 | MCB CAMP PENDLETON | 92055-5008 | SD | Lift Station 630121 | 0 | N/A | Power Failure | There was a loss of power to the lift station. | CORRECTION/ PREVENTION: A portable standby power generator with automatic transfer switch (ATS) was installed to provide backup power to the lift station. | N | N | Y | Talega Creek/San Mateo Creek | Pacific Ocean | Pacific Ocean | Y | Y | Y | 1000 feet North and South of San Mateo Beach | 6 | Flow traveled from wet well in a southwest direction to down drain culvert, approximately 100 feet to the shrubs and groundcover and mixed with the flood from Talega Creek. Total distance traveled was 4 miles. Public contact was expected.
45004 | Charles Cheng (voice) | 2005-01-13 13:05 | Mike Shope | (760) 725-9761 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2005-01-12 14:00 | 2005-01-12 16:10 | 300 | 39000 | 9750 | 29250 | Building 33832 | MCB CAMP PENDLETON | 92055-5008 | SD | Pump Station 33832 | 0 | N/A | Flood Damage | Due to the recent storm event, there was a break in the potable water line that runs across the Santa Margarita River. The water distribution to the 33 area was secured leaving the reservoir in a low level with low pressure. This caused all the flushometers to stick in the open position and automatically flush the water into the toilet bowl. The flushing water caused the wastewater collection system to flood. | CORRECTION: Flushometers were manually turned off in each building. Pumper trucks were used to minimize the impact of the spill volume. Since the water was chlorinated, there was no reason to disinfect the spill. PREVENTION: Fushometers will be checked when restoring pressure back to the potable water system. | Y | Y | Y | None | None | Overflow reached a dry channel and percolated into the ground. | Y | Y | Y | n/a | n/a | The wastewater spill from the old sewage treatment plant pumping station number 33832 and traveled approximately 1000 feet.
45005 | Quarterly Report | N/A | Christine Ricafrente | (760) 725-9761 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2005-03-01 08:00 | 2005-03-01 08:30 | 1.66 | 50 | 50 | 0 | Building 53323 | MCB CAMP PENDLETON | 92055-5008 | SD | Cleanout | 0 | N/A | Blockage | The cleanout from building 53323 overflowed due to paper towels and root blockage in the main sewer line. | CORRECTION: The main sewer line was jetted to remove blockage. A vacuum truck was used to recover the spill. Lime was spread on all the contaminated areas. PREVENTION: FMD will continue preventative maintenance of the sewage lines. | N | N | N | None | None | Overflow reached the lawn area at the backside of building 53323 | N | N | N | n/a | n/a | The spill traveled at the back side of building 53323, about 20 ft from the cleanout, and covered 20 square feet of the lawn area. Total distance traveled was 20 ft.
45006 | Charles Cheng (voice) | 2005-03-16 09:43 | Christine Ricafrente | (760) 725-9761 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 2005-03-16 08:00 | 2005-03-16 13:00 | 10 | 3000 | 2500 | 500 | Child Development Center, Building 1781 | MCB CAMP PENDLETON | 92055-5008 | SD | Cleanout under the building | 0 | n/a | Roots | The cleanout under building 1781 overflowed due to root blockage in the main sewer line. | CORRECTION: The main sewer line was jetted to remove root blockage. The spill was contained inside the crawl space underneath the building. The entire spill was pumped out and lime was spread on all contaminated areas. PREVENTION: Facilities Maintenance Department (FMD) will relocate the cleanout on the front side of the building to become visible and for easy access in the event of a spill. | N | N | N | None | None | Overflow did not reach actual receiving waters. The spill was contained in the building crawl space underneath the building. | Y | N | N | They were posted around the building. | They are still posted as of April 28, 2005. | All the children inside the building were evacuated upon learning that there was a sewage spill in the building. The spill was accumulated and contained inside the crawl space underneath the building. The contractor is still cleaning the site as of April 28, 2005. The building will remain close until the base Industrial Hygiene officer determines that the children are safe to comeback.
045004 | David Hanson | 2005-01-11 10:48 | Rich Arrant | (760) 744-0460 | Vallecitos Water District | Vallecitos Water District | 01/11/2005 0600 | 01/11/2005 1100 | 70 | 21000 | 0 | 21000 | Discovery St. | San Marcos | 92069 | SD | MH1142 | 0 | N/A | FLOOD DAMAGE | Infiltration | TV,Broken pipe replaced and grouted | Y | N | Y | San Marcos Ck | Pacific Ocean | N/A | Y | Y | Y | Carlsbad Beach | 7 | None
045005 | David Hanson | 02/21/2005 0830 | Rich Arrant | (760) 744-0460 | Vallecitos Water District | Vallecitos Water District | 02/21/2005 0730 | 02/21/2005 1315 | 152 | 52500 | 0 | 52500 | Discovery St. | San Marcos | 92069 | SD | MH1145 | 1 | 2005-01-11 | FLOOD DAMAGE | Infiltration | TV,and grouted | Y | N | Y | San Marcos Ck | Pacific Ocean | N/A | Y | Y | Y | Carlsbad Beach | 8 | Extended time to complete report ok By David Hanson
045006 | David Hanson | 2005-02-23 | Rich Arrant | (760) 744-0460 | Vallecitos Water District | Vallecitos Water District | 02/23/2005 0830 | 02/24/2005 0000 | 111.34 | 103550 | 0 | 103550 | Bent Ave. | San Marcos | 92069 | SD | MH1314 | 0 | N/A | FLOOD DAMAGE | Infiltration | Pipe up-size in progress | Y | N | Y | San Marcos Ck | Pacific Ocean | N/A | Y | Y | Y | Carlsbad Beach | 8 | None
0405012 | David Hanson, fax (858) 467-2952 | 2/22/2005 1301 | CS2 Dabney | 619-767-4893 | U.S. Navy Public Works | U.S. Navy Public Works | 2/22/2005 1301 | 2/22/2005 1345 | 2 | 90 | 0 | 90 | NBPL, Building 635 A, Page Rd. | San Diego | 92152 | SD | Pipe | 0 | N/A | BLOCKAGE | Line blocked due to solids clogging the line. Sewage came from lateral cover. | Line Hydroblasted | Y | Y | Y | San Diego Bay | N/A | San Diego Bay | Y | Y | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405013 | David Hanson, fax (858) 467-2952 | 2/24/2005 1230 | B. Witerington | 619-553-4142 | U.S. Navy Public Works | U.S. Navy Public Works | 2/24/2005 1230 | 2/24/2005 1430 | 2 | 250 | 50 | 200 | SUBASE, Bldg. 148, Strothe St. | San Diego | 92152 | SD | Pipe | 0 | N/A | BLOCKAGE | Line blocked due to solids clogging the line. Sewage came from lateral cover. | Line Hydroblasted | Y | Y | Y | San Diego Bay | N/A | San Diego Bay | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
0405014 | David Hanson, fax (858) 467-2952 | 3/15/2005 1530 | Mr. Patrol | 619-556-7349 | U.S. Navy Public Works | U.S. Navy Public Works | 3/15/2005 1515 | 3/15/2005 1517 | 1 | 1 | 0 | 1 | SUBASE, Pier 5000, Rosecrans St. | San Diego | 92152 | SD | Pipe | 0 | N/A | LINE BREAK | Leak in pipe feeding pier riser. | Repair Fitting | Y | Y | Y | San Diego Bay | N/A | San Diego Bay | Y | Y | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
045013 | 1(858) 571-6972 | 2005-05-19 14:50 | Mark Sanchez | (619)397- 6000 | City of Chula Vista | City of Chula Vista | 5/19/2005 1030 | 5/19/2005 1215 | 25 | 2625 | 250 | 2375 | Hunte Parkway and River Rock | Chula Vista | 91911 | SD | Sewer Manhole | 1 | 2004-08-30 | DEBRIS | Debris, concrete, rocks, wood from construction | Vacuumed debris from manhole, flushed and filmed sewer main | No | Yes | Yes | Salt Creek | N/A | Salt Creek | Yes | Yes | Y | Salt Creek basin from River Rock to Otay Lakes Road | Signs will be posted for five days | Blockage caused by construction debris (wood, concrete, large rocks). We were able to vacuum up debris flush line and film it. We will implement a maintenance program for that area to avoid future problems
045014 | 1(858) 571-6972 | 2005-05-24 12:50 | Mark Sanchez | (619)397- 6000 | City of Chula Vista | City of Chula Vista | 5/20/2005 UNKNOWN | 5/24/2005 1400 | 18 | 1320 | 200 | 1120 | Behind 563-565 Otis St. | Chula Vista | 91911 | SD | Sewer Cleanout | None | N/A | Blockage | Appears blockage was caused by paper | Notified landlord to call plumber and take care of problem. City washed down and vacuumed alley | No | Yes | No | N/A | N/A | Catch basin at end of alley | Yes | Yes | N | N/A | N/A | Private cleanout overflowed Storm Water Compliance Officers were notified by me. They called landlord to get plumber out to take care of problem. City washed down alley and vacuumed up, followed down to catch basin were sewage was contained due to debris in storm drain. Sewage never reached open storm drain.
045012 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-04-15 11:12 | 2005-04-15 12:30 | 0.38 | 30 | 30 | 0 | Ninth/C intersection | Coronado | 92118 | SD | Sewer Manhole | 0 |  | GREASE | Grease blockage in sewer main line | Jetted line and vactored out blockage. Scheduled videotaping of line. | N | N | N | None | None | Sewer system | Y | N | N | NA
045013 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-05-03 08:30 | 2005-05-03 12:00 |  | 220 | 220 | 0 | 101 B Avenue | Coronado | 92118 | SD | Sewer Vactor | 0 |  | OTHER | Solids in sewer vactor truck overflowed berm in pit in PS yard | Cleaned inlet, jetted line. Ensure that vactor solids are dumped weekly | N | Y | N | None | None | Sewer system | Y | N | N | NA
045014 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-06-11 01:00 | 2005-06-11 02:30 |  | 10 | 10 | 0 | 300 block Orange/C alley | Coronado | 92118 | SD | Sewer Main | 3 | 9-13-04, 12-11-04, 3-3-05 | ROOTS | Roots in sewer main caught paper and suspended solids, overflow from manhole | Removed roots, stepped up inspections until repaired | N | N | N | None | None | Sewer vactor | Y | N | N | NA |  | Sewer line is in CalTrans right of way. Permit for repairs received and replacement of line began mid-July
045015 | Quarterly Report |  |  |  | City of Coronado | City of Coronado | 2005-06-24 11:30 | 2005-06-24 13:30 | 1.39 | 125 | 75 | 50 | 8th and Coronado | Coronado | 92118 | SD | Sewer wet well | 0 |  | OTHER | Large volume of water discharged at once, surcharged system, caused overflow | Recovered majority of overflow, diverted storm drain system to sewer system to clear storm drain lines. Talked to discharger to ask that they not discharge large volumes at once | N | Y | N | None | None | Sewer system | Y | N | N | NA
045009 | Quarterly Report | 2005-05-16 09:30 | Called in by resident Gloria Rosenstein via Public Works and on to duty personnel David Zilberberg, Paul Thomas, Kip Curry, Peter Kiefer and Doug Blackstock | (858) 755-3294 | City of Del Mar | City of Del Mar | 2005-05-16 09:00 | 2005-05-16 10:30 | 1 | 90 | 90 | 0 | Manhole B5-18 (300 Blk of Luzon Avenue) | Del Mar | 92014 | SD | GIS Map page B5 Manhole B5-18 (300 Blk of Luzon Avenue) | 0 | N/A | ROOTS | Heavy roots in main | Rodded main with 4" auger followed by 6" auger: 140' x 2 from Manhole B5-17 to Manhole B5-18 | N | N | N | none | none | Main sewer line at Southfair B4-08 | Y | N | N | N/A | 0 | None
045003 | David Hanson | 2005-04-04 07:55 | Patrick Jackson | (619) 441-1658 | City of El Cajon | City of El Cajon | 2005-04-04 06:15 | 2005-04-04 06:30 | 1.6 | 25 | 0 | 0 | 700 BLK of Greenfield Dr. | El Cajon | 92020 | SD | MH 18-36 | 0 | N/A | Grease | Broken drop in manhole caused water to slow and allowed gease to build up | The broken drop in MH 18-40 is currently out to bid for a contractor to replace | N | N | N | None | None | Evaporated on roadway | Y | N | N | NA | 0 | None
045005 | David Hanson 858-571-2724 | 12/03/04 1145 | A.J Moeller | (619) 628-1372 | City of Imperial Beach | City of Imperial Beach | 11/03/04 1100 | 11/03/04 1205 | 0.5 | 30 | 25 | 5 | 550 HWY 75 | City of Imperial Beach | 91932 | SD | Cleanout #154A | 0 | None | BLOCKAGE | This was a partial blockage in a line servicing a hotel with three guests. | The downstream lines were cleaned as a precaution due to the dark debris cleaned out of the partially blocked line. | N | Y | Y | Pond 10A | None | Pond 10A | Y | N | N | N/A | 0 | It was recently found out that this is a ponding system used to make salt. Additionally, it is a wildlife preserve and is not subject to public use. The pond level is raised and lowered by a series of gates with the intention of draining Pond 20 for salt reclamation.
045014 | Victor Vasquez | 2005-04-11 11:00 | David Shissler | (949) 497-0328 | City of Laguna Beach | City of Laguna Beach | 2005-04-11 15:00 | 2005-04-11 15:15 | 1.67 | 25 | 0 | 25 | 329 Third St. | Laguna Beach | 92651 | OR | 4" private sewer lateral | N/A |  | PRIVATE PROPERTY | On April 11th at 3:00 p.m. I was notified of a plumbing problem at 329 Third Street. On scene at 3:15 p.m. I confirmed that the sewer lateral servicing 329 Third Street (Benson Plumbing) was plugged with evidence of approximately twenty-five gallons that had previously spilled from the sewer lateral cleanout cover. | Benson Plumbing was somewhat successful in clearing the blockage from the sewer lateral, which restored flow to the City's mainline but the lateral is still in need of repair. Dirt was observed on the tool used to clean the sewer lateral, this indicating a broken pipe. Permanent repairs to the sewer lateral were completed on April 12, 2005. | N | N | N | N/A | N/A | The estimated twenty-five gallons which spilled from the cleanout soaked into the dirt of the construction area with nothing to recover. | Y | N | N | N/A | N/A | Courtesy Report - Private Sewer Lateral | x
045015 | Brian Kelly | 2005-04-14 10:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-04-13 08:31 | 2005-04-13 09:31 | 0.33 | 20 | 0 | 20 | 1445 Temple Hills Dr. | Laguna Beach | 92651 | OR | Sewer lateral cleanout | 1 | 2004-05-24 | Roots | On Wednesday April 13, 2005 at 8:31p.m. staff received a call from Laguna Beach Police Department Dispatch alerting us to a sewer problem at 1445 Temple Hills Dr. Staff arrived on scene at 9:10 p.m. and confirmed that the sewer lateral servicing 1445 Temple Hills Dr. was plugged with evidence of approximately twenty gallons of sewage located around the cleanout cover. | Using a high pressure jetting machine, staff set-up at manhole # F23-091 jetting upstream to manhole #F23-078. A root blockage was encountered about 20ft. up into the main line, which we removed. This restored flow to the collection system. | N | N | N | N/A | N/A | The twenty gallons that had overflowed from the lateral cleanout soaked into the dirt. Staff removed a half bucket of dirt and debris. | Y | N | N | N/A | N/A | The sewage did not leave private property.
045016 | Victor Vasquez | 2005-04-28 14:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-04-28 05:47 | 2005-04-28 06:00 | 3.84 | 50 | 0 | 50 | 110 Anita St. | Laguna Beach | 92651 | OR | Anita St. Lift Station | 0 |  | Pump Station failure | Staff had been paged by the SCADA system that several lift stations were without power due to an Edison outage. At 5:46 a.m. they were also notified by the SCADA system that there was a pump failure at Anita Street Lift Station. Staff immediately responded and confirmed that there was a pump failure and the station manhole had overflowed, which resulted in an overflow to the Pacific Ocean. | Repairs were immediately made to the lift station motor and the CDS unit was taken off line from the collection system. | Y | N | Y | Pacific Ocean | N/A | Pacific Ocean | Y | N | Y | 150ft North & South of Anita St. Beach | 4 | 1419 Regatta Rd.
045017 | Victor Vasquez | 2005-05-04 09:10 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-05-03 13:05 | 2005-05-03 14:20 | 4 | 300 | 290 | 10 | 1704 Thurston Dr. | Laguna Beach | 92651 | OR | Manhole #F23-026 | 2 | 5/22/04, 4/15/05 | PRIVATE PROPERTY | On Tuesday, May 3, 2005 staff received a telephone call from Mrs. Eris Hirt who resides at 1677 Thurston Drive. Mrs Hirt informed staff that the sewer manhole was overflowing on Thurston Drive, which is a private street. The private contractor who was hired by the residents had broken the sewer manhole ring and cover the previous day and the debris had fallen in to the manhole, which had caused a blockage in the City's main line. | Staff cleared the debris from the manhole, which restored flow to the collection system. Using a high pressure jetting machine, staff cleaned the downstream City main lines and removed asphalt, rock and debris. Once the debris was removed, flow was restored to the main line. Staff placed traffic cones around the damaged area until the contractor could make the necessary repairs on May 5, 2005. | N | N | N | N/A | N/A | Three hundred gallons flowed above ground from manhole #F23-026 and flowed into manhole #F23-052. | Y |  | N | N/A | N/A | Staff did a follow-up on May 4 and all repairs had been completed. | x
045018 | Victor Vasquez | 2005-06-01 10:45 | Bernadette McCusker | (949) 497-0342 | City of Laguna Beach | City of Laguna Beach | 2005-06-01 06:50 | 2005-06-01 06:55 | 6 | 870 | 0 | 870 | Bluebird Canyon Dr. Area | Laguna Beach | 29651 | OR | Multiple City Main Lines & manholes | 1 | 2004-07-18 | Debris | On June 1, 2005 City crews were notified of a landslide that was occurring in the Bluebird Canyon Drive area. Crews responded to the scene, but due to the catastrophic nature of the landslide, crews were unable to access the area. During the first three hours of the landslide, 350 homes were evacuated and water service shutoff throughout the entire canyon area. City administrative staff contacted the OCHCA, OES, SOCWA and San Diego Regional Board to make them aware of the problem. As a precaution, the OCHCA closed Bluebird Beach 500 ft. north and 100ft. south. | Sewer crews were able to access the area after 9 a.m. and were able to determine that 35 homes had been affected with 29 of these homes having leaked sewage. Seventeen of the 29 homes have been destroyed and it is forecasted that the 12 remaining homes will have sewer service restored within the next ten days. Three manholes were also destroyed in the landslide area. Three temporary lift stations have been set up (see remarks column for locations). It is estimated that these lift stations will be in operation for a minium of two years. | N | Y | Y | Open Canyon Area at Bluebird | Pacific Ocean | Pacific Ocean | Y | Y | Y | Bluebird Canyon Beach | 3 | The temporary lift stations are located as follows: 1. 1085 1/4 Bluebird Canyon Dr. 2. 1020 1/4 Madison Place 3.1074 1/4 Flamingo Road The volume amount was calculated as followes: 6 gals per min. x 5 mins duration x 29 homes =870 gallons.
045019 | Victor Vasquez | 2005-06-14 10:00 | Graham Wright | (949) 497-0765 | City of Laguna Beach | City of Laguna Beach | 2005-06-13 21:00 | 2005-06-13 22:20 | 3.125 | 250 | 0 | 250 | 1419 Regatta Rd. | Laguna Beach | 92651 | OR | Private Sewer Cleanout | 1 | 2004-11-04 | Roots | At 9:00 p.m. on June 13, 2005 Gregg Barton received notification from the Laguna Beach Police Dispatch that a sewer spill was occurring at 1419 Regatta Road. Staff arrived on scene at 9:30 p.m. Laguna Beach Police and Fire were also on scene and informed us that a sewer backup was occurring in the lower portion of a home at 1419 Regatta Road. | Using a vacuum truck, Staff pumped water from manhole #G24-09 to visually determine the source of the problem and to relieve the surcharged condition from the system. After evacuating the water from the manhole, it was apparent that the source of the blockage was caused by tree roots blocking the downstream outlet of the manhole. Staff removed the roots and debris which restored flow back to the collection system at 10:20 p.m. | N | Y | N | Open Canyon Area | N/A | Open Canyon Area | Y | N | N | N/A | N/A | The overflow from the cleanout went down a hillside, entered a concrete “V” ditch and into a storm drain. Efforts to recover the water from the storm drain were not feasible due to the location of the storm drain outlet which feeds into an open canyon area.
045017 | Victor Vasquez | 05/28/05 1355 | Mike Dumas | 7604355842 | City of Oceanside | City of Oceanside | 05/28/05 1120 | 05/28/05 1205 | 10 | 450 | 50 | 400 | 3755 Via Campana | Oceanside | 92054 | SD | Manhole | 1 | 2004-10-09 | DEBRIS | Line is broken and debris accumulates behind the offset area. | Replacement of line has pased the design phase and has gone to bid. | N | Y | N | Drainage ditch. | None | Manhole spilled into a drain that daylights into a canyon with little or no access. | Y | N | N |  |  | Timing of line replacerment has taken longer than expected due to purchase of new City Easement.
045018 | Victor Vasquez | 06/12/05 1516 | Agung Mertha | 7604355842 | City of Oceanside | City of Oceanside | 06/12/05 1235 | 06/12/05 1305 | 25 | 750 | 0 | 750 | 4987 Delos Way | Oceanside | 92056 | SD | Manhole | 0 |  | ROOTS | Roots infiltrated grade rings from large tree nearby. | All manhjoles in area being TVd, and roots being removed. | N | N | N | None | None | Soil in large grassey area maintain by HOA Saturated soil impossible to enter with Vactor Truck. | Y | N | N
045019 | Victor Vasquez | 06/19/05 1210 | Scott Rogers | 7604355842 | City of Oceanside | City of Oceanside | 06/19/05 0953 | 06/19/05 1030 | 3 | 111 | 111 | 0 | 517 South Barnwell | Oceanside | 92056 | SD | Manhole | 0 |  | GREASE | Residential area grease blockage. | Cleaned line. Dropped 100 Lbs. of Chlorine to "burn out" line. | N | N | N | None | None | Full recovery with Vactor. | Y | N | N
| Fax | 2005-04-01 14:30 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2005-04-01 09:30 | 2005-04-01 10:30 | 3 | 200 | 60 | 140 | 265 W. Marquita | San Clemente | 92672 | OC | Private sewer system | 2 | 08/06/2005 03/15/2005 | OTHER | Broken sewer lateral | Contractor repaired sewer line | N | N | N |  |  | Soaked into surrounding soil | Y | N | N |  |  | Private sewer system | x
| Voice Mail | 2005-06-29 10:00 | Jay Elston | 949-366-1553 | City of San Clemente | City of San Clemente | 2005-06-28 13:20 | 2005-06-28 14:30 | 1 | 80 | 50 | 30 | 219 W. Marquita | San Clemente | 92672 | OC | Private sewer system | 0 |  | BLOCKAGE | Private sewer system blockage | Contractor repaired sewer line | N | Y | Y |  |  | Pacific Ocean | Y | N | Y | Mariposa beach San Clemente | 4 | Private sewer system | x
045001 | Bryan Ott FAX (858) 571-6972 | 2005-06-20 15:30 | Danny King | (858) 720-2477 | City of Solana Beach | City of Solana Beach | 2005-06-20 11:15 | 2005-06-20 11:30 | 33 | 500 | 0 | 500 | 632 N. Granados | Solana Beach | 92075 | SD | Manhole | 0 | 0 | other | Massive injection of clean water by local water agency, Santa Fe Irrigation District, (SFID) flushing new lines nearby, introducing too much water for sewer system to handle | As soon as overflow detected, water agency shut down water. City called out vactor truck to clear the line as precaution. City staff and SFID will discuss their practices to ensure this will not happen again | N | Y | N | San Elijo Lagoon | None | Catch basin. Not enough entered to impact the lagoon. | Y | N | N | N/A | 0
045033 | faxed | 2005-04-02 17:00 | Richard Flynn | 760.726-1340 | City of Vista | City of Vista | 2005-04-02 08:46 | 2005-04-02 10:14 | 325 | 28600 | 0 | 28600 | S. Melrose Drive at Green Oak Road | Vista | 92081 | SD | City of Vista | N/A | N/A | Vandalism | Manhole structure V33173 located under So. Melrose over crossing was vandalized with 12" +/- boulders, logs, broken glass. | Ongoing scheduled preventive maintenance installation of locked sewer lids and visual monitoring. | N | N | Y | Aqua Hedionda Creek/Buena Creek | None | N/A | N | Y | Y | So. Melrose O/C to south/west to beach | Still posted | The initial report received by reporting party stated MH overflow was located at Antigua Duck Pond which is 1-2 miles west of actual spill area. Aqua Hedionda Creek was flowing 500-600 GPM as measure using stick and time method.
045034 | faxed | 2005-04-16 18:30 | Richard Flynn | 760.726-1340 | City of Vista | City of Vista | 2005-04-16 14:06 | 2005-04-16 15:35 | 5 | 450 | 425 | 25 | Buena Vista Drive | Vista | 92081 | SD | Unknown | N/A | N/A | Vandalism | Several large boulders were placed inside the City of Vista manhole located 1000 feet east of Buena Vista Road | Update this area with a current map; install a locking lid and locks on gates and do frequent preventative maintenance inspections. | N | N | N | None | None | Dirt easement road and cow pasture | Y | N | Y | Access gates | 3
045035 | faxed | 2005-04-29 15:00 | George Solano | 760.726-1340 | Buena Sanitation District | Buena Sanitation District | 2005-04-29 07:04 | 2005-04-29 08:02 | 5 | 290 | 200 | 90 | 1441 York Drive | Vista | 92083 | SD | B13 MH 49 | N/A | N/A | Roots | Roots have heavily infiltrated this sewer line | Place this line on a 3-month hot spot cleaning cycle. Because of the heavy rains, the hot spot cleaning for this line was delayed by 1-month. The City of Vista will award bid of contract to repair this line in August 2005. | Y | N | Y | York Drive low lying area | Open marsh area | Open marsh/grass area downstream of spill. Spill did not reach established creek. | Y | N | Y | 1000' in each direction of spill | Still posted | Samples taken of creek upstream and downstream. Crews vacuumed all accessible areas of spill. Approximately 90 gallons seeped into the lower marshy area.
045036 | faxed | 2005-05-29 17:49 | Richard Flynn | 760.726-1340 | Buena Sanitation District | Buena Sanitation District | 2005-05-29 17:49 | 2005-05-29 18:33 | 1 | 45 | 45 | 0 | 1975 Yettford Drive | Vista | 92084 | SD | B13 MH 186 | 1 | 2005-01-09 | Roots | Struck a root blockage at 256' from downstream manhole B13 MH 188 | Increase preventative maintenance cycle, survey condition of line segment. | N | N | N | None | None | Roadway and gutter | Y | N | N | N/A | N/A | Emergency response crew washed right-of-way and gutter and vacuumed and disposed discharge back to sewer system.
045037 | faxed | 2005-06-15 21:00 | Jimmy Rodriguez | 760.726-1340 | City of Vista | City of Vista | 2005-06-15 19:25 | 2005-06-15 21:30 | 15 | 1725 | 1000 | 725 | 3555 Winslow Road | Oceanside | 92054 | SD | OV2 MH 29-30 | N/A | N/A | Grease | Grease blockage in the mainline. | Chain flailed line to remove grease from this line. Put line on a routine hot spot list. | N | Y | Y | Calaveras Lake | None | N/A | Y | N | Y | Post at spill site per Clay Clifton | 2 | Post signs at a minimum of 72 hours.
005004 | FAX | 2005-04-13 11:00 | L Schempp | (760) 753-0155 | Leucadia County Water District | Leucadia County Water District | 2005-04-13 10:20 | 2005-04-13 10:30 | 1 | 10 | 0 | 10 | North Coast Hwy | Carlsbad | 92009 | SD | B3-020 Air Vac | 0 | NA | OTHER | Air Vac failed to reseat completely | Isolated, Inspected, and Serviced | N | N | N | NA | NA | Water Contained on Bridge Platform | Y | N | N | NA | 0 | None
045004 | FAX (858) 571-6972 | 2005-05-02 09:30 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2005-04-29 17:15 | 2005-04-29 17:45 | 0 | 10 | 5 | 5 | Del Avion/Niguel Rd. | Laguna Niguel | 92677 | OR | Manhole #1, Sta. 1+00, Sect. Pg. E32/F32 | 0 | 0 | Grease | Partial grease blockage causing manhole to overflow onto parking lot. | Jetter cleared stoppage. Hose and vacuum parking lot and curb area to clean up. Video inspection found NO irregularities in pipe. | N | Y | Y | Salt Creek | NONE |  | Y | N | N
045005 | FAX (858) 571-6972 | 2005-06-09 08:00 | Brad Bruington | (949) 425-3543 | Moulton Niguel Water District | Moulton Niguel Water District | 2005-06-08 20:15 | 2005-06-08 21:20 | 5 | 350 | 50 | 300 | Near 28901 La Lita | Mission Viejo | 92691 | OR | Manhole #14 MNWD sectional page J21 | 0 | 0 | DEBRIS | Manhole had 14 sandbags, umbrella, rocks, bricks, etc., causing partial blockage | Debris removed. Sewer line cleaned (jetted) both directions. Sewer line video inspected - nothing found. Manhole lid replaced with locking lid. Incident report to O.C. Sheriff's Dept. | N | N | Y | Trabuco Creek | Pacific Ocean, Doheny Beach |  | Y | N | Y |  |  | Warning signs were already posted
045004 | Bryan Ott/Brian Kelly | 2005-04-14 16:00 | Barry Gerrity | 760-788-2239 | Ramona Municipal Water District | Ramona Municipal Water District | 2005-04-14 15:15 | 2005-04-14 15:25 | 200 | 2000 | 0 | 2000 | 22758 San Vicente Rd. | Ramona | 92065 | SD | Chlorine Contact Mixer | 1 | 2005-03-18 | Power Failure | While draining for repair, coupling came undone. | Better connection for future work. | N | N | N | N/A | none | Dirt easement | Y | Y | N | N/A | 0 | None
045005 | Brian Ott/Clay Clifton | 2005-06-27 11:40 | James Gusman | 760-788-2262 | Ramona Municipal Water District | Ramona Municipal Water District | 06/27/05 07;15 | 2005-06-27 08:10 | 1 | 55 | 55 | 0 | 24157 San Vicente Road | 24157 San Vicente Road | 92065 | SD | MH 86 | 1 | 2004-01-11 | GREASE | Grease from restaurant | Cleared Blockage and Re-ran with Warthog nozzle to clean line | N | N | N | N/A | N/A | Recovered from cart path | Y | N | N | N/A | 0 | None
045001 | Left Message | 4/15/2005,14:30 | David Holguin | (951) 296-6900 | Rancho California Water District | Rancho California Water District | 4/15/2005,11:45 | 4/15/2005,12:45 | 25 | 1500 | 0 | 1500 | 41476 Patri Circle | Murrieta | 92562 | RV | 66 | 0 | 0 | GREASE | Grease and Sand blockage. | Used Vactor/Combination truck to relieve blockage, Jet Rodded 300 feet up and downstream. | N | Y | Y | Tributary to Murrieta Creek. | none | Overflow entered a storm channel which eventually leads to Murrieta Creek. | Y | Y | Y | Entrance of tributary on Valor Drive. | 7
045006 | FAX 858-571-6972 | 2005-04-12 15:00 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-04-06 | 2005-04-06 14:30 | 0 | 30 | 0 | 30 | 31341 Ceanothus Dr | Laguna Beach | 92651 | OC | Lateral line | 0 | NONE | ROOTS | Private sewer lateral backed up. District crews found roots growing in private lateral at approximately 70 ft downstream from clean out access although the clean out was not overflowing when District crews arrived. | District crew used hydro jetter 3/4" hose to flush away roots. Crews also ran a flexible snake with 4" cutter and pulled out a large amount of roots. District crew set a debris trap at downstream manhole and jetted the main line. | N | N | N | n/a | n/a | Saturated into ground (sandy landscaped area). No sewage left the property. | Y | N | n/a | n/a | 0 | Private System Overflow Incident | x
045007 | FAX 858-571-6972 | 2005-04-13 16:05 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-04-08 15:00 | 2005-04-08 18:00 | 0 | 300 | 300 | 0 | 33601 Del Obispo | Dana Point | 92629 | OC | Private lateral 4" cleanout | 0 | NONE | GREASE | District crews found sewage running down the parking lot coming from a cleanout within the Albertsons shopping center. | District crews put down sandbags and a spill containment mat at storm drain entry. Spill was contained and did not enter storm drain. District crew used one combination jetter truck at the storm drain location to vacuum sewage runoff. Another jetter was used to jet the private line from the south end manhole of the property. Crew ran approximately 270' from manhole to the grease trap. A plumber snaked the cleanout and cleared the blockage of heavy grease buildup. District crew vacuumed the grease from the grease trap., pressure washed the parking lot and vacuumed up the excess flow and cleaned up the overflow area to prevent further spread of residual sewage. Property owner/management company was notified and SCWD met with them onsite to assist in development of maintenance plan to prevent future SSO's. | N | N | N | n/a | n/a | n/a | Y | N | n/a | n/a | 0 | Private System Overflow Incident | x
045008 | FAX 858-571-6972 | 2005-04-26 11:30 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-04-21 09:50 | 2005-04-21 10:10 | 0 | 15 | 15 | 0 | 26246 Via Canyon | Capistrano Beach | 92624 | OC | Private lateral 4" cleanout | 0 | NONE | ROOTS | District crews noticed the overflowing cleanout. Crew contained the spill at entry of the downstream storm drain by laying down a spill containment mat and setting a combination jetter truck to vacuum the runoff. | Plumber ran the snake and cleared the blockage as well as videod the lateral. After plumber cleared the lateral, District crew jetted the main line. They also ran the video camera in the main line to verify that the line was in good condition. | N | N | N | n/a | n/a | n/a | Y | N | n/a | n/a | 0 | Private System Overflow Incident | x
45009 | FAX 858-571-6972 | 5/18/200514:35 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 5/13/200510:45 | 2005-05-13 15:15 | 0 | 500 | 0 | 500 | 74 N. La Senda | Laguna Beach | 92651 | OC | Line break | 0 | NONE | LINE BREAK | District crews found a broken 6" cast iron sewer service lateral sheared off at face of cliff. | An approximate 15' section of PVC pipe was used to connect to the existing lateral inside the tunnel to the broken end of lateral on cliff face. Also supports were used inside the tunnel to support the weight of the cast iron lateral. District crew will install a new pipe from Adit door to the main trunk line inside the tunnel. | N | N | Y | Pacific Ocean | n/a | n/a | Y | N | Y | 300 ft at the south end of 10th Avenue | 3 days | Private System Overflow Incident
45010 | FAX 858-571-6972 | 2005-05-18 14:10 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2004-05-14 13:30 | 2005-05-14 14:15 | 0 | 50 | 50 | 0 | 24676 Morning Star Lane | Dana Point | 92629 | OC | Manhole | 0 | NONE | ROOTS | District crews found a manhole overflowing (located within private residential development). Cause of the overflow appeared to be roots, grease and mud. Crews used dirt from around the landscape area to build a beam to contain the overflow. | After containing the spill and cleaning up the area, District crews spoke with the management company and instructed them to video the line and make the necessary repairs and to have a maintenance program in place to prevent backups/overflows from occurring again. | N | N | N | n/a | n/a | n/a | Y | N | n/a | n/a | 0 | Private System Overflow Incident
45011 | FAX 858-571-6972 | 2005-06-30 07:45 | Joseph McDivitt | 949-499-4555 | South Coast County Water District | South Coast County Water District | 2005-06-14 09:00 | 2005-05-14 17:00 | 0 | 30 | 0 | 30 | 17 Camel Point | Laguna Beach | 92651 | OC | Lateral line | 0 | NONE | BLOCKAGE | District crews found service lateral overflowing. The 4" service lateral is a cast iron pipe. When it was being cleaned with the jetter, the residual flow was very black, which is an indication of the scale buildup being dislodged from the pipe walls. | After cleaning the lateral a video camera was used to evaluate the condition of the service lateral. The cast iron pipe did have heavy scale buildup. District crew spoke with the owner to make him aware of the condition of the lateral and to make him aware of the necessary repairs needed to prevent this type of incident from happening in the future. | N | N | N | n/a | n/a | Overflow saturated into hillside | Y | N | n/a | n/a | 0 | Private System Overflow Incident | x
045002 | Brian Kelly | 2005-06-23 | Kris Hanberg | 949-858-0277 | Trabuco Canyon Water District | Trabuco Canyon Water District | 2005-06-23 09:00 | 2005-06-23 10:30 | 2000 | 60000 | 60000 | 60000 | Santa Margarita Pkwy | Mission Viejo | 92692 | OC | n/a | 0 | n/a | Line Break | Water Hammer | Check operation of pumps and surge tank | n | y | y | Oso Creek | none | Oso Barrier | y | y | N | N/A | 0
045007 | QUARTERLY REPORT |  | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 4/2/05 07:00 | 4/2/05 10:30 | 0.95 | 200 | 75 | 125 | Building 43520 | Camp Pendleton | 92055-5008 | SD | Building 43520 cleanout | 0 | n/a | ROOTS | For several days, the toilets have been backing up and water coming up through the floors in Building 43520. On Saturday morning (4/2/2005), the cap to the sewer cleanout was removed. Sewer flowed out of the cleanout. | The cap for the sewer cleanout was put back in place. Treated sewer line with root-x. Jet clean sewer line from cleanout to manhole. | N | Y | N | none | none | Overflow did not reach actual receiving waters but: Percolated into grass lawn and ponded in storm drain inlet | N | N | N | n/a | 0 | n/a
045008 | QUARTERLY REPORT |  | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/2/05 04:30 | 5/2/05 08:00 | 0.24 | 50 | 0 | 50 | Lift Station 31220 | Camp Pendleton | 92055-5008 | SD | Lift Station 31220 | 0 | n/a | OTHER | Failure of the pressure relief valve caused an intermittent spray at times when the air pressure vented. | Pressure relief valve was isolated. Maintenance request was submitted to shop 34. Valves and vents will be monitored. | N | N | N | none | none | Overflow did not reach actual receiving waters but: Ponded on concrete within the lift station footprint | N | N | N | n/a | 0 | n/a
045009 | Brian Kelley 858-467-4254 | 5/6/05 08:50 | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/5/05 09:50 | 5/5/05 11:50 | 60 | 7200 | 1000 | 6200 | Lift Station 31220 | Camp Pendleton | 92055-5008 | SD | Lift Station 31220 | 1 | 05/02/05 | OTHER | Pressure relief valve on the discharge line failed and resulted in a spill. | Pressure relief valve isolated at shut-off valve. Pressure relief valve was replaced. The valve was plumbed to drain to the wet well to help ensure that any potential future leaks do not escape the system. | N | N | Y | Santa Margarita River | Pacific Ocean | n/a | Y | Y | N | n/a | 0 | n/a
045010 | Brian Kelley 858-467-4254 | 5/13/05 16:00 | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/13/05 08:30 | 5/13/05 10:00 | 111.11 | 10000 | 4300 | 5700 | Force Main near Bldg 410306 | Camp Pendleton | 92055-5008 | SD | Force Main near Bldg 410306 | 0 | n/a | LINE BREAK | The force main joint blew from the pressure in the line. | The pump station upstream from the broken force main was shut down. The wastewater was diverted to a pump truck while the force main was being repaired. | N | Y | N | none | none | Overflow did not reach actual receiving waters but: Percolated into grass field and ponded in storm drain inlet | Y | Y | Y | The five signs were posted around grassy field where the spill ponded/ percolated. | 7 | n/a
045011 | Brian Kelley 858-467-4254 | 5/13/05 16:00 | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/13/05 10:30 | 5/13/05 11:30 | 8.33 | 500 | 500 | 0 | Manhole behind Building 520430 | Camp Pendleton | 92055-5008 | SD | Manhole behind Building 520430 | 0 | n/a | VANDALISM | Large rocks were found in the manhole. | FMD used pumper truck to jet out rocks in the line. | N | N | N | none | none | Overflow did not reach actual receiving waters but: Ponded on the asphalt and absorbed by mattresses | Y | N | N | n/a | 0 | n/a
045012 | QUARTERLY REPORT |  | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/19/05 12:45 | 5/19/05 13:30 | 6.67 | 300 | 50 | 250 | Pump Station 31227 | Camp Pendleton | 92055-5008 | SD | Pump Station 31227 | 0 | n/a | PUMP STATION FAILURE | The air relief valve failed and pump #3 became air locked. Pumps # 1 and 2 were also air locked. The flow valves didn't register the problem. The PC circuit board failed to send the alarm for the other pumps to come on. | The pump was unlocked. The PC circuit board was replaced with a new controller. | N | N | N | none | none | Overflow did not reach actual receiving waters but: Ponded on the side of the dirt road | N | N | N | n/a | 0 | n/a
045013 | VOICEMAIL 858-627-3930 | 5/29/05 12:00 | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 5/28/05 12:20 | 5/28/05 13:30 | 13.57 | 950 | 700 | 250 | Manhole near Building 22186 | Camp Pendleton | 92055-5008 | SD | Manhole near Building 22186 | 0 | n/a | BLOCKAGE | At Lift Station 22188, there are three pumps - one of the pumps was clogged with rags, the second pump was air locked, and the third pump could not keep up with the flow. This caused the wastewater to back up and to overflow through a manhole. | The first pump was pulled out and the blockage removed. The second pump was unlocked. Lift Station 22188 is scheduled to be upgraded/ replaced. | N | Y | N | none | none | Overflow did not reach actual receiving waters but: Dry vegetated earthen storm drainage channel | Y | N | N | n/a | 0 | n/a
045014 | VOICEMAIL 858-627-3930 | 6/4/05 9:02 | Joann Lim | 760-725-9762 | U.S. Marine Corps, Camp Pendleton | U.S. Marine Corps, Camp Pendleton | 6/4/05 10:22 | 6/5/05 12:30 | 5 | 1500 | 0 | 1500 | Lift Station 63012 | Camp Pendleton | 92055-5008 | SD | Lift Station 63012 Wet Well | 1 | 01/11/05 | DEBRIS | Due to debris in the wet well, the bubbler line, that measures the water depth in the wet well, was pinched off and caused the wet well pump to run until it shut off due to internal heat. With the pump shut off, the wet well overflowed. | The wet well was pumped out. | N | N | Y | dry creek bed (Christianitos Creek) | none | n/a | Y | Y | N | n/a | 0 | The spill ended on 6/4/05 at 12:42 but restarted later on 6/5/05 at 09:50.
045007 | Brain Kelley | 2005-05-25 15:57 | Corey Harrell | (760)744-0460 | Vallecitos Water District | Vallecitos Water District | 2005-05-25 12:45 | 2005-05-25 13:10 | 150 | 3750 | 3750 | 0 | Mission Rd. | San Marcos | 92069 | SD | MH1722 | 0 | N/A | LINE BREAK | Collapsed while cleaning | Broken pipe was replaced | N | Y | N | None | None | N/A | Y | Y | N | N/A | 0 | None
0405015 | N/A | 6/6/2005 1400 | Mr. Robert Witherington | 619-571-4282 | U.S. Navy Public Works | U.S. Navy Public Works | 6/6/2005 1400 | 6/6/2005 1445 | 1.5 | 60 | 0 | 60 | Roserans near bldg. #215 | San Diego | 92152 | SD | manhole | 0 | N/A | Blockage | Blockage of line by roots and debris. | Cleared line. | N | N | N | N/A | N/A | ground | Y | N | N | N/A | N/A | Site was cleaned up as per PWC sewer spill clean up SOP.
423216 | Fax (858) 571-6972 (RWQCB) | 2004-10-04 15:23 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-07-07 20:00 | 2004-07-08 06:23 | 170 | 105400 | 0 | 105400 | 2411 Dairy Mart Rd. So. Bay Reclamation Plant | San Diego | 92154 | SD | 36" RCP | 0 |  | PUMP STATION FAILURE | wet well level float stuck on low, low level pump support | moved level floats away from pump support. Also replaced broken impeller and installed a redundant level indicator. | N | Y | N | None | None | ran into the brush and dried up in dirt track. | Y | Y | N |  | 0 | This report was entered by Jeff Wilder per hand written copy from O&M for data recording only. No notifications or faxing done.
426103 | Fax (858) 571-6972 (RWQCB) | 2004-07-12 10:10 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-07-11 09:20 | 2004-07-11 09:50 | 0.5 | 15 | 0 | 15 | 8402 HIGH WOOD DR | San Diego | 92119 | SD | 8"VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | MACHINE RODDED TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORMDRAIN SYSTEM. | Y | Y | N |  | 0 | Incorrect S.R. number used. New S.R. Number is 426103. Old S.R. number is 425980
426104 | Fax (858) 571-6972 (RWQCB) | 2004-07-12 10:10 | Alberto Mejia | (858) 654-4135 | City of San Diego | City of San Diego | 2004-07-11 11:10 | 2004-07-11 11:50 | 0.5 | 20 | 0 | 20 | LORING ST & SOLEDAD RD (KATE SESSIONS PKNG LOT) | San Diego | 92109 | SD | 6"VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | MACHINE RODDED TO RELIEVE ROOT STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | DRIED IN CURB AREA ON SOLEDAD RD | Y | Y | N |  | 0 | Wrong sr# 425981. Correct sr# 426104
428159 | Fax (858) 571-6972 (RWQCB) | 2004-07-15 14:55 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-07-14 07:44 | 2004-07-14 08:23 | 35 | 1365 | 1200 | 165 | 2600 Truxtun Rd. | San Diego | 92140 | SD | 8" V.C. | 0 | 0 | ROOTS | Roots and paper towels caused spill | Contractor had storm drain blocked with sand bags prior to city crews arrival. Rodded & flushed main to clear blockage. Vacuumed spill at storm drain inlet. | N | N | N | None | None | Dissipated in construction site grounds. | Y | Y | N |  | 0 | No sewer was observed inside storm drain at time of investigation. Spill was contained at 08:20 and releived at 09:04.
430343 | Fax (858) 571-6972 (RWQCB) | 2004-07-15 22:34 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-07-15 20:05 | 2004-07-15 21:16 | 5 | 355 | 355 | 0 | GARNET AVE. X PICOST. | San Diego | 92109 | SD | 8" VC | 0 |  | GREASE | GREASE IN CITY SEWER MAIN. | VACTORED OVERFLOW. RODDED AND FLUSHED MAIN TO RELEIVE BLOCKAGE AND CLEAN.. REFER TO HAVE PIPE TELEVISED. | N | Y | N | None | None | RETURNED TO SEWER SYSTEM VIA INTERCEPTOR 9. | Y | Y | N |  | 0
431222 | Fax (858) 571-6972 (RWQCB) | 2004-07-18 13:15 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-07-18 10:31 | 2004-07-18 11:03 | 3 | 96 | 0 | 96 | 6535 42ND ST | San Diego | 92113 | SD | 8" VC | 0 | 0 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | UNIT 718 CONTAINED OVERFLOW UPON ARRIVAL; UNIT 724 RODDED MAIN TO RELIEVE STOP; REFER TO TV VIA STBY FOREMAN & TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N |  | 0
434529 | Fax (858) 571-6972 (RWQCB) | 2004-07-28 10:45 | Melody Shaw | (858) 614-5772 | City of San Diego | City of San Diego | 2004-07-21 10:05 | 2004-07-21 11:40 | 10 | 950 | 0 | 950 | 5987 Baja Drive | San Diego | 92115 | SD | 8" C. P. | 1 | 03/07/2004 | FLOOD DAMAGE | The cause of the spill was due to a mainbreak. | Rodded to releive stoppage, will refer to area supervisor for further evaluation and to be televised for possible 724. | N | N | N | None | None | Dissipated in canyon grounds | Y | Y | N |  | 0 | The main has been televised as of 7-28-04- The cause of the spill was due to a mainbreak.
439769 | Fax (858) 571-6972 (RWQCB) | 2004-07-30 14:10 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-07-30 11:39 | 2004-07-30 12:15 | 1 | 36 | 0 | 36 | 2335 Boundary.St | San Diego | 92104 | SD | 6" CP Main | 1 | 01/06/2004 | ROOTS | Roots and grease blockage were found in the city main. | We relieved the blockage in the main and cleaned for city protection , and referred to be televised on 7-30-2004 . | N | N | N | None | None | Dissapated in grass curb area. | Y | Y | N |  | 0
441555 | Fax (858) 571-6972 (RWQCB) | 2004-08-05 08:35 | Melody Shaw | (858) 614-5772 | City of San Diego | City of San Diego | 2004-08-04 10:29 | 2004-08-04 11:41 | 5 | 360 | 0 | 360 | Kensington Dr & Alder.St | San Diego | 92116 | SD | 10"VC - Main | 0 |  | FLOOD DAMAGE | 10" VC Main break | Set up containment and vactored cleaned up spill area, called out construction crew to make repairs on 10" main. Referred to CCTV to televise the main .Clean main for city protection | N | Y | N | None | None | Dissapated in stormdrain/soil. | Y | Y | N |  | 0
445909 | Fax (858) 571-6972 (RWQCB) | 2004-08-12 23:30 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-08-12 22:09 | 2004-08-12 23:25 | 3 | 228 | 0 | 228 | 1960 IRVING AVE. | San Diego | 92113 | SD | 6" VC | 0 |  | GREASE | GREASE IN CITY SEWER MAIN. | RODDED MAIN TO RELIEVE BLOCKAGE. REFER TO HAVE FURTHER CLEANING DONE IN AM. REFER TO HAVE MAIN TELEVISED. | N | N | N | None | None | CONTAINED ON FENCED LOT BETWEEN 1944 AND 1960 IRVING AVE. | N | Y |  |  | 0 | BLOCKAGE ON CITY SEWER MAIN CAUSED PROPERTY LATERAL C/O TO OVERFLOW ON FENCED VACANT DIRT LOT. US MH 552, FSN102427; DS MH 20, FSN102096.
447861 | Fax (858) 571-6972 (RWQCB) | 2004-08-18 18:15 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2004-08-18 14:31 | 2004-08-18 16:17 | 5 | 530 | 330 | 200 | Camto Cantilena X Paseo Monte Batalla | San Diego | 92128 | SD | 8' VC | 0 |  | OTHER | Heavy paper towels caused stoppage. | Set up containment, rodded to relieve, cleaned main, cleaned up street. Will have area cleaned by main cleaning crew in a.m. | N | Y | N | None | None | Dissapated in storm drain system | Y | Y |  |  | 0 | Upsream MH 28, FSN 116234, Down srtream MH 29, FSN 116235 were 4 sections down stream from the overflowing MH 27 in gated community.
448277 | Fax (858) 571-6972 (RWQCB) | 2004-08-31 13:30 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2004-08-19 15:07 | 2004-08-19 16:45 | 1 | 98 | 0 | 98 | 1819 LYNDON RD. | San Diego | 92103 | SD | 6" CP | 0 |  | LINE BREAK | VANDALISM. PIECE OF CARPET AND ROCKS IN SEWER MAIN. | HAND RODDED TO REMOVE CARPET AND ROCKS. REFER TO HAVE SEWER MAIN TELEVISED. | N | N | N | None | None | SOAKED INTO GROUND NEAR MAIN C/O. | Y | Y |  |  | 0 | 6" CITY C/O ON EASEMENT MAIN. 64' SECTION NEEDS TO BE TELEVISED WITH LATERAL CAMERA. NO MH AT CONNECTION POINT TO THROUGH MAIN. TELEVISE UP AND DOWN STREAM SECTIONS FROM CONNECTION POINT ON THROUGH MAIN (FSN 23454, 23481).
448384 | Fax (858) 571-6972 (RWQCB) | 2004-08-20 08:00 | James Wiley | (858) 614-5820 | City of San Diego | City of San Diego | 2004-08-19 09:30 | 2004-08-19 13:00 | 0.017 | 3.57 | 0 | 3.6 | 2802 Dairy Mart .Rd | San Diego | 92173 | SD | Carbon Canister | 0 |  | LINE BREAK | The spill was caused by a leak in a 60 gal carbon canister.Due to corrosion. | Removed leaky canister and replace with a new canister. | N | N | N | None | None | Dissapated in the sand area | Y | Y |  |  | 0 | City crews were conducting their routine preventive maint/ and discovered the leak and took the corrective actions to resove the promblem.
448402 | Fax (858) 571-6972 (RWQCB) | 2004-08-20 14:30 | Isaac Y. Jenkins | (858) 614-5770 | City of San Diego | City of San Diego | 2004-08-20 08:40 | 2004-08-20 10:00 | 1 | 80 | 60 | 20 | Intersection of Mission Gorge and Mission Montana Dr. | San Diego | 92124 | SD | 8pvc | 0 |  | GREASE | Heavy Grease plug Manhole 213 downstream scoop relieved stoppage | Set up Containment, check manholes relieved stop, Flushed main and wash down street after retrieving sewage and refer to be televised | N | Y | N | None | None | Heat evaporation and settled in dirt filled storm drain | Y | Y |  |  | 0 | Grease passing through system cause a stoppage at manhole # 213.
448724 | Fax (858) 571-6972 (RWQCB) | 2004-08-22 14:25 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-08-22 11:25 | 2004-08-22 11:44 | 5 | 95 | 30 | 65 | 3190 LANDIS ST | San Diego | 92104 | SD | 8" PVC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSH LINE TO RELIEVE GREASE STOP; VACUUM STANDING SEWAGE FROM ALLEY & CLEAN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y |  |  | 0
450493 | Fax (858) 571-6972 (RWQCB) | 2004-08-26 22:17 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-08-26 17:39 | 2004-08-26 19:20 | 1 | 101 | 20 | 81 | 3460 MARTIN AVE. | San Diego | 92113 | SD | 8" VC | 0 |  | ROOTS | ROOTS AND PAPER DEBRIS CAUSING BLOCKAGE IN CITY SEWER MAIN. | FLUSHED MAIN TO REMOVE ROOTS AND DEBRIS. REFER TO HAVE MAIN TELEVISED. | N | Y | N | None | None | DRIED IN STORM BOX AT END OF ALLEY. | N | Y | N |  | 0 | BLOCKAGE IN MAIN FLOODED HOUSE, AND OVERFLOWED FROM PROPERTY C/O, SPILLING INTO ALLEY. US MH 317, DS MH 316.
451362 | Fax (858) 571-6972 (RWQCB) | 2004-09-01 15:45 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2004-09-01 11:29 | 2004-09-01 13:30 | 3 | 363 | 200 | 163 | 6150 El Cajon Blvd. | San Diego | 92115 | SD | 6" VC | 0 |  | ROOTS | Roots in easement main caused overflow | 748 investigated area found 7-31 out from 6150 El Cajon Blvd. where sump pump was discharging overflow. Most of overflow was contained on property. Relieved stop and vacuumed puddles and deodorized area.Called to have main TV'd | N | Y | N | None | None | Dissapated in storm drain system. | Y | Y | N |  | 0
451734 | Fax (858) 571-6972 (RWQCB) | 2004-09-02 14:30 | Isaac Y. jenkins | (858) 614-5770 | City of San Diego | City of San Diego | 2004-09-02 10:33 | 2004-09-02 11:45 | 2 | 144 | 120 | 24 | 3723 Columbia St. | San Diego | 92103 | SD | 6"cp | 0 | 0 | LINE BREAK | main stoppage cause laterals to back up unknown source of debri or object (no roots or grease found) | Upon arrival contain sewer by building a dam, vactor up access sewer clean up driveway and street area by washing down. Clear stoppage. | N | Y | N | None | None | Storm drain at India and Winder were it dried up. | Y | Y | N |  | 0 | Source of stoppage unknown retrieved nothing of value. Referred to TV.
452142 | Fax (858) 571-6972 (RWQCB) | 2004-09-03 15:00 | Isaac Y. Jenkins | (858) 614-5770 | City of San Diego | City of San Diego | 2004-09-03 11:28 | 2004-09-03 14:20 | 1 | 172 | 172 | 0 | 842 TONYE ST. | San Diego | 92105 | SD | 6"VC | 0 | 0 | ROOTS | Stoppage was cause by a combination of light roots and grease | Contained spill to curbside area vactor and wash down area. Relieved stoppage | N | N | N | None | None | Curbside then into vactor machine | N | Y | N |  | 0
453341 | Fax (858) 571-6972 (RWQCB) | 2004-09-13 11:35 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-09-11 19:02 | 2004-09-12 10:00 | 0.25 | 224.5 | 0 | 224.5 | 4201 06TH AVE | San Diego | 92103 | SD | 8"vc | 0 | 0 | ROOTS | Possible 7-24; roots in pipe caused sewage to flow out of ground. | Investigate BSO call on 9-11-04; No BSO Found. Return in am 9-12-04 & determined 7-31 out of ground; poss 7-24; referred to TV; Rodded to clear d/e main. Referred to area supervisor for further evaluation. | N | N | N | None | None | SOAKED INTO CANYON. | Y | Y | N |  | 0
453422 | Fax (858) 571-6972 (RWQCB) | 2004-09-15 10:00 | Jeff Wilder | (858) 614-5770 | City of San Diego | City of San Diego | 2004-09-13 09:46 | 2004-09-13 10:30 | 2 | 88 | 28 | 60 | 15 Th & Broadway | San Diego | 92101 | SD | 6" Main VC | 0 |  | FLOOD DAMAGE | After TV of main, primary cause was determined to be a main break causing rags and plastic basgs to hang up and block main. | The stoppage was relieved rodded,vactored , flushed. The spill area was disinfected for city protection, and has been referred to be televised | N | N | N | None | None | Dissapated in street | Y | Y | N |  | 0 | Revision due to televising the main and determining that there was a main break causing the debris to hang up and block the flow. Report was re-faxed.
453995 | Fax (858) 571-6972 (RWQCB) | 2004-09-15 23:37 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-09-15 16:25 | 2004-09-15 19:10 | 3 | 495 | 400 | 95 | IMPERIAL AVE. X WOODMAN ST. | San Diego | 92113 | SD | 15" VC | 0 |  | ROCKS | ROCKS IN SEWER MAIN. | FLUSHED AND VACTORED MAIN TO RELIEVE OVERFLOW. REMOVED LARGE ROCKS WITH HAND TOOLS. WILL REFER TO HAVE MAIN TELEVISED TO ASSESS PIPE CONDITION. | N | N | N | None | None | DIRT STORM CULVERT NEAR SE CORNER IMPERIAL X WOODMAN | Y | Y | N |  | 0
454687 | Fax (858) 571-6972 (RWQCB) | 2004-09-21 15:37 | JORGE HERNANDEZ | (858) 654-4130 | City of San Diego | City of San Diego | 2004-09-20 18:05 | 2004-09-20 18:30 | 1 | 20 | 0 | 20 | FAY AV X KLINE AV | San Diego | 92037 | SD | 8" PVC | 0 |  | GREASE | GREASE IN CITY SEWER MAIN. | RODDED AND FLUSHED MAIN TO REMOVE BLOCKAGE AND CLEAN PIPE. REFFER MAIN TO BE TELEVISED. | N | Y | N | None | None | DRIED IN STORM BOX AT 5592 FAY AV. | Y | Y | N |  | 0
455333 | Fax (858) 571-6972 (RWQCB) | 2004-09-23 13:50 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-09-23 09:54 | 2004-09-23 11:19 | 4 | 340 | 0 | 340 | 1442 Myrtle.Ave | San Diego | 92103 | SD | 6"CP Main | 0 |  | ROOTS | Roots were found in the main. | Hand rodded to relieve blockage , and flushed for city protection, televised the pipe . | N | N | N | None | None | Dissapated in dirt/ Canyon. | Y | Y | N |  | 0
455645 | Fax (858) 571-6972 (RWQCB) | 2004-09-27 09:00 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-09-24 16:30 | 2004-09-24 17:40 | 5 | 350 | 0 | 350 | 3730 SWIFT AVE | San Diego | 92104 | SD | 8"VC | 0 | 0 | ROCKS | BLOCKAGE WAS CAUSED BY ROCKS LEFT IN MAIN BY CONTRACTOR (ORION CONST) INSTALLING NEW MAIN UPSTREAM. | UNABLE TO LOCATE DOWNSTREAM M/H; SET UP ON UPSREAM M/H & RODDED; UNIT 718 CONTAINED OVERFLOW AT 17:40; UNIT 724 RELIEVED STOP AT 18:50; CLAIMS CONTACTED FOR HEAVY 7-31 IN. STBY NOTIFIED TO SEND TV UNIT TO INSPECT MAIN & POSSIBLY LOCATE M/H. | N | Y | N | None | None | DISSIPATED IN STORMDRAIN SYSTEM. | Y | Y | N |  | 0
455740 | Fax (858) 571-6972 (RWQCB) | 2004-09-27 09:30 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-09-25 09:03 | 2004-09-25 09:20 | 20 | 340 | 0 | 340 | 3810 WABASH AVE | San Diego | 92104 | SD | 8"PVC | 1 | 09-24-2004 | CONSTRUCTION | ROCK; GRAVEL; 6" PVC ELBOW; LEFT IN MAIN BY CONTRACTOR (ORION CONST) INSTALLING NEW MAIN | ROD MAIN TO RELIEVE STOP CAUSED BY CONSTRUCTION DEBRIS; CALL FOR FLUSHER TO FLUSH ALL LINES IN AREA; REFER TO TV AND AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N |  | 0 | Area under construction & changes not yet shown in field book.
455909 | Fax (858) 571-6972 (RWQCB) | 2004-09-28 14:55 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-09-27 10:50 | 2004-09-27 11:00 | 2 | 20 | 0 | 20 | 6033 Fenimore.Way | San Diego | 92108 | SD | 8" VC Main | 0 |  | ROOTS | Roots caused blockage in city main. | Rodded main to relieve blockage, flushed for city protection,disinfected area and referred main to be televised by CCTV. | N | Y | N | None | None | Dissapated in stormdain . | Y | Y | N |  | 0 | Unit 712 was doing PM maintaint in the area and noticed the manhole overflowing and immediate begain to relieve blockage in city main.
456577 | Fax (858) 571-6972 (RWQCB) | 2004-09-30 11:15 | Melod Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-09-30 08:51 | 2004-09-30 10:10 | 2 | 158 | 0 | 158 | 1842 Clove.St | San Diego | 92107 | SD | 6"CP | 1 | 04/04/2004 | ROOTS | Roots blockage in main was the primary cause. | The main was rodded to relieve root blockage,dissinfected area of spill,and referred to CCTV. | N | Y | N | None | None | Dissipated in stormdrain | Y | Y | N |  | 0
456656 | Fax (858) 571-6972 (RWQCB) | 2004-09-30 19:55 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-09-30 16:06 | 2004-09-30 17:15 | 1 | 69 | 0 | 69 | 5635 OLVERA AV. | San Diego | 92113 | SD | 6" CP | 0 |  | ROOTS | ROOTS GROWING IN CITY SEWER MAIN. GREASE ACCUMULATION. | FLUSHED AND RODDED MAIN TO RELIEVE BLOCKAGE AND CLEAN MAIN. REFER MMAIN TO BE TELEVISED. | N | N | N | None | None | SOAKED INTO DIRT EASEMENT AT OVERFLOWING MH 51. | Y | Y | N |  | 0
457010 | Fax (858) 571-6972 (RWQCB) | 2004-10-03 11:00 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-10-03 09:01 | 2004-10-03 09:26 | 2 | 50 | 40 | 10 | 4405 VANDEVER AVE | San Diego | 92120 | SD | 8:VC | 0 | 0 | GREASE | BLOCKAGE WAS CAUSED BY GREASE. | FLUSHED LINE TO RELIEVE GREASE STOP; SET UP ON DOWNSTREAM M/H AND VACUUMED UP SPILL; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | Unit vacuumed from stormdrain; some dissipated in system. | Y | Y | N |  |  | This report was entered by Jeff Wilder per hand written copy from O&M for data recording only. No notifications or faxing done.
458454 | Fax (858) 571-6972 (RWQCB) | 2004-10-09 20:15 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-10-09 18:05 | 2004-10-09 18:45 | 0.5 | 20 | 10 | 10 | 3714 MISSION BLVD | San Diego | 92109 | SD | 6"VC | 1 | 05/30/2004 | GREASE | BLOCKAGE WAS CAUSED BY GREASE | FLUSHED LINE TO RELIEVE GREASE STOP; CLEAN AREA; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | SMALL AMOUNT DRIED IN STORM DRAIN | Y | Y | N |  |  | Incorrect S.R. number used. New S.R. Number is 426103. Old S.R. number is 425980
458517 | Fax (858) 571-6972 (RWQCB) | 2004-10-11 11:53 | Melody Shaw for M.Oregel | (858) 614-5772 | City of San Diego | City of San Diego | 2004-10-11 07:47 | 2004-10-11 08:25 | 1 | 38 | 30 | 8 | 5216 College. Gardens. Court | San Diego | 92115 | SD | 8"VC | 1 | 02/05/2004 | ROOTS | There was a rootball found in the ctiy main. | Rodded main to relieved blockage referred to CCTV , flushed for city protection. | N | Y | N | None | None | Dry up in Canyon Ground | Y | Y | N |  |  | Wrong sr# 425981. Correct sr# 426104
460306 | Fax (858) 571-6972 (RWQCB) | 2004-10-16 19:50 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-10-16 16:06 | 2004-10-16 17:00 | 5 | 270 | 0 | 270 | 9067 HILLERY DR | San Diego | 92126 | SD | 8"VC | 0 | 0 | GREASE | BLOCKAGE CAUSED BY GREASE. | UNIT 719 SET UP CONTAINMENT AT 17:00; UNIT 718 RELIEVED THE STOP AT 17:30; ALL OVERFLOW FROM 1700 TO TIME STOP RELIEVED WAS CAPTURED & RETURNED TO SYSTEM; AREA CLEANED; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | DISSIPATED IN STORM DRAIN SYSTEM. | Y | Y | N
461136 | Fax (858) 571-6972 (RWQCB) | 2004-10-26 11:15 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-10-20 05:00 | 2004-10-21 10:30 | 11 | 19470 | 0 | 19470 | 5602 Dartford Way | San Diego | 92120 | SD | 8"VC MAIN | 0 |  | ROOTS | ROOTS FOUND IN MAIN. | Rodded the main to relieve blockage,and cleaned main for city protection, referred to be televised,and cleaned up spill area. | Y | Y | Y | San Diego River | Alvarado Creek Channel | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach | 5
460970 | Fax (858) 571-6972 (RWQCB) | 2004-10-20 14:30 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-10-20 12:00 | 2004-10-20 12:30 | 5 | 150 | 0 | 150 | 4752 Adelphi Pl. | San Diego | 92115 | SD | 8" V. C. | 0 | 0 | ROOTS | Heavy roots caused blockage in 8" main | Machine rodded to clear blockage, Called CCTV to televise main. Will be refer to area supervisor for further action. | Y | Y | N | None | None | Dissipated in canyon grounds. | Y | Y | N |  | 0
461658 | Fax (858) 571-6972 (RWQCB) | 2004-10-23 15:30 | Carlos E. Gomez Tagle | (858) 654-4142 | City of San Diego | City of San Diego | 2004-10-23 10:43 | 2004-10-23 11:50 | 10 | 530 | 530 | 0 | 4231 1/2 42nd st | San Diego | 92105 | SD | 6" vc | 1 | 01/26/2004 | ROCKS | Blocage was cause by rocks and sand. | Unit 724 rodder main from the down/stream MH221, Unit 718 vaccumed contained sewer at the street storm drain and at Fairmount Av by the concrete storm drain. Unit 724 relieved stop at 11:50. Contacted TV unit to ispect main. Unit 749 cleaned street. | N | y | n | None | None | back into the system after contained and vaccumed it. | y | Y | N
462002 | Fax (858) 571-6972 (RWQCB) | 2004-10-26 09:10 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-10-26 01:23 | 2004-10-26 02:20 | 1 | 57 | 25 | 32 | 8422 Summerdale Road | San Diego | 92126 | SD | 8" V. C. | 0 | 0 | GREASE | Very heavy grease blockage in main caused clean out to spill. | City crew flushed to clear main and clean up small spill area. Will refer to area supervisor for further evaluation and to be televised. | N | N | N | None | None | Dissipated into the ground. | Y | Y | N |  | 0
462433 | Fax (858) 571-6972 (RWQCB) | 2004-10-27 21:53 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-10-27 10:30 | 2004-10-27 10:50 | 60 | 1200 | 0 | 1200 | PACIFIC HWY X FRIARS RD. | San Diego | 92101 | SD | JUNCTION STRUCTURE | 0 |  | OTHER | HIGH FLOWS IN SMI AND SM2. | SLOWED DISCHARGE FROM SPS 1, AND INCREASED DISCHARGE FROM SPS 2. | Y | N | Y | SAN DIEGO RIVER | PACIFIC OCEAN | N/A | Y | Y | N |  |  | BLOCKAGE ON CITY SEWER MAIN CAUSED PROPERTY LATERAL C/O TO OVERFLOW ON FENCED VACANT DIRT LOT. US MH 552, FSN102427; DS MH 20, FSN102096.
462295 | Fax (858) 571-6972 (RWQCB) | 2004-11-04 21:34 | C. MICKELSONl | (858) 654-4130 | City of San Diego | City of San Diego | 2004-10-27 06:30 | 2004-10-27 09:25 | 57 | 9975 | 0 | 9975 | Governor Dr. & 1-805 SB Off Ramp | San Diego | 92122 | SD | 15" V. C. | 0 | 0 | ROOTS | Infiltration at Miramar Marine Corp Air Station cause surcharge of Miramar Trunk Sewer Just west of I805 | Began By pass pumping at Manhole 54 | Y | N | Y | RoseCreek | Pacific Ocean | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach | 9 | Upsream MH 28, FSN 116234, Down srtream MH 29, FSN 116235 were 4 sections down stream from the overflowing MH 27 in gated community.
463192 | Fax (858) 571-6972 (RWQCB) | 2004-11-01 15:15 | M.Shaw for J. Lindsay | (619) 221-8771 | City of San Diego | City of San Diego | 2004-10-27 11:52 | 2004-10-27 12:13 | 107619 | 2259999 | 0 | 2259999 | 1902 Gatchell. Rd Pt Loma Wastewater Trt Plant | San Diego | 92106 | SD | PT.Loma Trt Plant | 0 |  | ROOTS | Influent flow exceeded peak design, barscreens and blinded | We opened the overflow weirs in order for the barscreens to start operating properly. | Y | Y | Y | Pacific Ocean | None | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach | 6 | 6" CITY C/O ON EASEMENT MAIN. 64' SECTION NEEDS TO BE TELEVISED WITH LATERAL CAMERA. NO MH AT CONNECTION POINT TO THROUGH MAIN. TELEVISE UP AND DOWN STREAM SECTIONS FROM CONNECTION POINT ON THROUGH MAIN (FSN 23454, 23481).
462936 | Fax (858) 571-6972 (RWQCB) | 2004-10-30 15:30 | Carlos E. Gomez Tagle | (858) 654-4142 | City of San Diego | City of San Diego | 2004-10-30 09:07 | 2004-10-30 12:00 | 10 | 1730 | 1730 | 0 | 655 Pons st | San Diego | 92114 | SD | 8" VC | 0 |  | LINE BREAK | Blockage was caused by a 8" ball made by platic yellow and grey tape with foam inside. | Roder removed the object from the main, flusher vacuumed sewer spill coming from the inside of the property and cleaned street. Refer to area supervisor for evaluation. Reported vandalism to SDPD report #04-067248. | N | n | n | None | None | vacuumed and back to the system. | n | Y | N |  |  | City crews were conducting their routine preventive maint/ and discovered the leak and took the corrective actions to resove the promblem.
463180 | Fax (858) 571-6972 (RWQCB) | 2004-11-01 14:00 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-11-01 10:41 | 2004-11-01 11:16 | 1 | 35 | 0 | 35 | 175 Benson Street | San Diego | 92114 | SD | 8" V. C. | 2 | 12/04/2003 & 02/02/2004 | ROOTS | Roots in main caused overflow in private clean out | Flushed & root saw to clear main. Deodorized and clean area. | N | N | N | None | None | Dissipated in gutter | Y | Y | N |  | 0 | Property owner took clean out lid off to avoid an overflow inside her house.
464106 | Fax (858) 571-6972 (RWQCB) | 2004-11-05 12:10 | Marcelino Oregel | (858) 614-5719 | City of San Diego | City of San Diego | 2004-11-05 09:17 | 2004-11-05 09:36 | 2 | 38 | 0 | 38 | 5328 Pirotte Drive | San Diego | 92105 | SD | 6" V. C. | 0 | 0 | CONSTRUCTION | Sanitary paper and a piece of C.P. in main caused blockage. | Flushed main to releive blockage and clean pipe. Refer to have pipe televised and to area supervisor for further evaluation. | N | Y | N | None | None | Dissipated in storm drain system | Y | Y | N |  | 0
464720 | Fax (858) 571-6972 (RWQCB) | 2004-11-09 22:35 | C. MICKELSON | (858) 654-4130 | City of San Diego | City of San Diego | 2004-11-09 16:24 | 2004-11-09 19:00 | 0.25 | 39 | 10 | 29 | 3635 DUPONT ST. | San Diego | 92106 | SD | 6" VC | 0 |  | ROOTS | ROOTS GROWING INTO DE MAIN C/O STACK. | UNABLE TO RELIVE BLOCKAGE BY MACHINE RODDING DE MAIN. HAND RODDED FROM DE MAIN C/O, REMOVING HEAVY ROOTS GROWING IN STACK. REFERRED TO HAVE MAIN AND C/O TELEVISED. | Y | N | N | None | None | NW CORNER SILVER GATE AV. X DUPONT ST. | Y | Y | N |  |  | BLOCKAGE IN MAIN FLOODED HOUSE, AND OVERFLOWED FROM PROPERTY C/O, SPILLING INTO ALLEY. US MH 317, DS MH 316.
465540 | Fax (858) 571-6972 (RWQCB) | 2004-11-11 10:00 | Linda Ruiz - Lopez | (858) 428-1306 | City of San Diego | City of San Diego | 2004-11-10 14:04 | -655963.3597 | 1 | 18 | 0 | 18 | Dairy Mart. Rd | San Diego | 92154 | SD | N/A | 0 |  | OTHER | Rags caused the screens to clog the check valve… | Secured BSL pump 1& 2 called emergency stand-by crew and notified the emergency pipe crew to make repairs on valve and clean. | N | N | Y | Tijuana River | None | Tijuana River and creeek grounds | Y | Y | N
465112 | Fax (858) 571-6972 (RWQCB) | 2004-11-13 12:15 | Carlos E. Gomez Tagle | (858) 654-4142 | City of San Diego | City of San Diego | 2004-11-12 13:41 | 2004-11-12 14:40 | 2 | 122 | 0 | 122 | 5459 Moonlight | San Diego | 92037 | SD | 8" VC | 0 |  | ROOTS | Blockage was caused by heavy roots in main. | Unit 724 rodder sewer main relieved stop. Claims contacted for clean-up backyard. Stby notified to send TV unit for inspection. | N | n | n | None | None | Spread out and soaked into the backyard soil. | N | Y | N |  |  | Revision 14a, on 11/12/04 unable to confirm number of spill locations within 1000'. On 11/13/04 final total spill locations is 0. Changes on 3, 4: date time reported and reported by and phone.
465977 | Fax (858) 571-6972 (RWQCB) | 2004-11-18 12:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-11-18 07:00 | 2004-11-18 07:00 | 0.15 | 3 | 1 | 2 | Dairy Mart Rd X Mesa Creek Bridge | San Diego | 92154 | SD | n/a | 1 | 11/11/04 | BLOCKAGE | blockage cause due to rags in air valve screen | removed rags from screen clean spray air valve . | N | N | Y | Mesa Creek | None | Ground & Creek | Y | Y | N
465997 | Fax (858) 571-6972 (RWQCB) | 2004-11-18 14:45 | Melody Shaw-Sydnor | (858) 614-5772 | City of San Diego | City of San Diego | 2004-11-18 13:01 | 2004-11-18 13:25 | 1 | 24 | 0 | 24 | 4166 Euclid. Ave | San Diego | 92115 | SD | 6" concret/pipe | 0 |  | BLOCKAGE | Heavy tissue paper -school near spill location | City crew rodded the main , cleaned up area called the claims dept for property damages,referred to cctv to televise main. | N | N | N | None | None | Dissapated in street | Y | Y | N
466845 | Fax (858) 571-6972 (RWQCB) | 2004-11-24 11:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-11-24 08:35 | 2004-11-24 09:15 | 3 | 120 | 0 | 120 | 1920 Carmelina Dr | San Diego | 92108 | SD | 8"VC Main | 1 | 11/03/2004 | CONSTRUCTION | Toilet paper and industrial rags | Flushed and cleaned city main to relieve blockage , refer to Area Supervisor, and CCTV to televise city man. | N | N | N | None | None | Soaked into park grounds | Y | Y | N |  | 0 | Revision due to televising the main and determining that there was a main break causing the debris to hang up and block the flow. Report was re-faxed.
466898 | Fax (858) 571-6972 (RWQCB) | 2004-11-24 16:00 | Daryl Wehrham | (619) 428-7314 | City of San Diego | City of San Diego | 2004-11-24 12:15 | 2004-11-24 12:17 | 1 | 2 | 0 | 2 | Dairy mart Rd | San Diego | 92154 | SD | N/A | 3 |  | OTHER | Check Valve not fully seated Debries accumulated in check valve | Isolated valve and notified pipeline crew to make repairs . | N | N | N | None | None | Ground surface next to valve | Y | Y | N |  | 0
467323 | Fax (858) 571-6972 (RWQCB) | 2004-11-29 15:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-11-29 11:00 | 2004-11-29 13:10 | 50 | 6500 | 2500 | 4000 | 2159 Haniman Dr | San Diego | 92105 | SD | 6'' VC | 1 | 11/05/2004 | GREASE | Heavy Grease And Roots | Flushed and Machined Rodded Clean up area , Refer to area supervisor and CCTV to televise main per policy. | Y | Y | N | None | None | Soak in dirt and Vegetation in canyon in Chollas Creek Area. | Y | Y | N |  | 0
467961 | Fax (858) 571-6972 (RWQCB) | 2004-12-01 22:35 | Jeff Wilder | (858) 654-4130 | City of San Diego | City of San Diego | 2004-12-01 14:41 | 2004-12-01 17:30 | 0.5 | 84.5 | 37.5 | 47 | 945 S. Euclid Ave. | San Diego | 92113 | SD | 8"VC | 0 |  | ROOTS | Roots in main caused grease to build up and stop flow in main causing overflow from cleanout. | Vacummed overflow, flushed to relieve stop, cleaned two sections up and one section down, will refer for TV. | N | Y | N | None | None | Dissipated in storm drain | Y | Y | N
468053 | Fax (858) 571-6972 (RWQCB) | 2004-12-02 09:30 | Jose L oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-02 07:25 | 2004-12-02 08:00 | 20 | 700 | 0 | 700 | Dancy Pl X Dancy Rd | San Diego | 92126 | SD | 8'' pvc | 1 | 09/02/2000 | GREASE | Grease and debries block flow in 8'' pvc main | flush 8'' pvc main relief grease and debries blockage clean up spill site refer to CCTV to tv 2 up and 2 down per City policy refer to area supervisor. | N | Y | N | None | None | Soak in Canyon | Y | Y | N |  | 0
468940 | Fax (858) 571-6972 (RWQCB) | 2004-12-07 16:45 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-07 14:17 | 2004-12-07 15:26 | 3 | 207 | 130 | 77 | 2271 01 Street | San Diego | 92134 | SD | 6''VC | 2 | 01/07/2004,06/29/2004 | GREASE | Grease Blockage | Machine rodded to relief stoppage and flush mains 2 up and 2 down per City policy , CCTV responded refer to area Supervisor | Y | Y | N | None | None | Desipated in Storm Drain System. | Y | Y | N |  | 0 | Area under construction & changes not yet shown in field book.
470084 | Fax (858) 571-6972 (RWQCB) | 2004-12-14 21:00 | Jeff Wilder | (858) 654-4130 | City of San Diego | City of San Diego | 2004-12-14 18:08 | 2004-12-14 19:08 | 2 | 120 | 50 | 70 | 3054 Mercer Ln. | San Diego | 92122 | SD | 8" VC | 0 |  | ROOTS | Roots in main | Set up vacuum to recover and contain overflow, rodded to relieve stop, flushed four up stream sections and one down stream section. Referred to be TVd. | N | Y | N | None | None | Soaked into canyon | Y | Y | N |  |  | Unit 712 was doing PM maintaint in the area and noticed the manhole overflowing and immediate begain to relieve blockage in city main.
470419 | Fax (858) 571-6972 (RWQCB) | 2004-12-16 21:15 | Jeff Wilder | (858) 654-4130 | City of San Diego | City of San Diego | 2004-12-16 17:02 | 2004-12-16 17:55 | 5 | 265 | 50 | 215 | 554 Los Angeles Pl. | San Diego | 92113 | SD | 8'' PVC | 1 | 3/27/2004 | OTHER | 8" screw caused grease to build up and block main. | Set up containment, flushed to relieve stop, retrieved 8" screw, called claims for clean up in backyard of address. Referred to TV | N | N | N | None | None | Dissipated in gutter | Y | Y | N |  | 0
470375 | Fax (858) 571-6972 (RWQCB) | 2004-12-16 13:15 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-16 10:45 | 2004-12-16 12:50 | 1 | 125 | 0 | 125 | 7145 Fairway dr | San Diego | 92037 | SD | 8'' VC | 1 | 12/08/2004 | ROOTS | 8'' vc main blockage | flusher relieved root stoppage refer to area supervisor and CCTV to tv as per City Policy 2up and 2 down from fsn#2972-10 . | N | N | N | None | None | Soak into dirt area by sewer main | Y | Y | N |  | 0
470505 | Fax (858) 571-6972 (RWQCB) | 2004-12-17 15:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-17 09:30 | 2004-12-17 10:20 | 1 | 50 | 0 | 50 | Ashland Av X Hillgrove Dr | San Diego | 92120 | SD | 8'' VC | 0 |  | BLOCKAGE | sewer main blockage | flush main , CCTV main 2 up an 2 down refer to area supervisor | N | Y | N | None | None | Disipeted in storm drain | Y | Y | N |  | 0
470557 | Fax (858) 571-6972 (RWQCB) | 2004-12-17 19:20 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-12-17 15:51 | 2004-12-17 16:35 | 25 | 1100 | 0 | 1100 | 5715 STREAMVIEW DR | San Diego | 92105 | SD | 8"VC | 1 | 1 | ROOTS | BLOCKAGE WAS CAUSED BY ROOTS. | SET UP CONTAINMENT; INVESTIGATE; FLUSHED LINE TO RELIEVE STOP CAUSED BY ROOTS. CLEAN AREA. REFFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | Y | N | None | None | SOAKED INTO GROUND AT CHOLLAS PKWY & QUINCY ST. | Y | Y | N
471078 | Fax (858) 571-6972 (RWQCB) | 2004-12-22 13:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-22 09:35 | 2004-12-20 11:10 | 5 | 475 | 0 | 475 | 2324 Sumac Dr | San Diego | 92105 | SD | 8'' VC | 0 |  | BLOCKAGE | blockage was cause by heavy grease | flushed main to relieve grease stoppage also clean 2 up and 2 down as per city policy call for CCTV and refer to Area Supervisor . | N | N | N | None | None | Backyard | Y | Y | N |  | 0
472085 | Fax (858) 571-6972 (RWQCB) | 2004-12-31 01:30 | Jorge Hernandez | (858) 654-4130 | City of San Diego | City of San Diego | 2004-12-30 22:17 | 2004-12-30 23:40 | 5 | 415 | 0 | 415 | 5603 cervantes av | San Diego ca. | 92113 | SD | 10''pvc | 0 |  | GREASE | grease in sewer main | flushed main,and releive blockage,will refer to televise main | N | y | n | None | none | dissipated in storm drain | y | Y | N |  |  | stop was between mh 163 and169,cleaned two sections up,two down
472018 | Fax (858) 571-6972 (RWQCB) | 2004-12-30 15:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2004-12-30 12:20 | 2004-12-30 13:30 | 3 | 210 | 0 | 210 | 506 Palomar Ave | San Diego | 92037 | SD | 6'' CP | 0 |  | BLOCKAGE | Sewer line grease blockage | rodded 6'' cp main relieved blockage in fsn# 876 refer to area supervisor and CCTV to tv 2 up and 2 down as per policy | Y | N | N | None | None | Backyard | Y | Y | N |  | 0 | revised council District #
472121 | Fax (858) 571-6972 (RWQCB) | 2004-12-31 12:50 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2004-12-31 07:41 | 2004-12-31 10:40 | 50 | 8950 | 0 | 8950 | CASS ST & VAN NUYS (IN CANYON) | San Diego | 92109 | SD | 8"VC | 1 | 11/12/2004 | ROOTS | ROOT BLOCKAGE. | DIRT ROAD IN CANYON WASHED AWAY; HYLINE RODDER CABLE TO M/H AND ROD TO RELIEVE ROOT BLOCKAGE; POST SIGNS AT TOURMALINE STATE PARK ON BOTH SIDES OF STORMDRAIN OUTLET; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | Y | PACIFIC OCEAN | None |  | Y | Y | Y | TOURMALINE SURFING PARK
472221 | Fax (858) 571-6972 (RWQCB) | 2005-01-19 10:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-01-09 22:40 | 2005-01-10 02:10 | 25 | 5250 | 0 | 5250 | Governor Dr X I-805 SB Off Ramp | San Diego | 92122 | SD | 15'' VC | 1 | 11/04/04 | ROOTS | Infiltration at Miramar Marine Corp Air Station Cause Surcharge Of Miramar Truck Sewer Just west of I-805 | Continue by pass pumping at full throttle . | Y | N | Y | Rose Creek | Pacific Ocean | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach |  | Signs were remove on 01/19/05 at Mission Bay Park,Campland on The Bay,Crown Point Shores,Vacation Isle,Hidden Anchorage,South Shores,Enchanted Cove,Leisure Lagoon & Crown Point.as requested by Clay Clifton with San Diego County Department..
474700 | Fax (858) 571-6972 (RWQCB) | 2005-01-19 10:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-01-11 04:40 | 2005-01-11 15:20 | 50 | 32000 | 0 | 32000 | Rose creek X Miramar Rd | San Diego | 92122 | SD | 15'' VC | 2 | 11/04/04 01/10/05 | ROOTS | Infiltration At Miramar Corp Ar Station Cause Surcharge Of Miramar Trunk Sewer Just West of I-805 | Continue By Pass Pumping at Full Throttle | Y | N | Y | Rosecreek | Pacific Ocean | Pacific Ocean | Y | Y | Y | Bay/Lagoon/Beach |  | Signs were remove at Crown Point,Vacation Isle,Leisure Lagoon,Enchanted Cove,South Shores & Hidden Anchrorage as requested by Clay Clifton with the San Diego County Department Of Environment Health Dept.
474772 | Fax (858) 571-6972 (RWQCB) | 2005-01-11 13:45 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-01-11 10:45 | 2005-01-11 11:30 | 20 | 900 | 600 | 300 | 6886 Birchwood St | San Diego | 92120 | SD | 10'' VC | 0 |  | GREASE | Heavy Grease blocking 10''VC Main | flush FSN# 50215 to relieved heavy Grease, Refer to Area Supervisor and CCTV for tv 2 up and 2 down after 733. | Y | Y | N | None | None | Canyon | Y | Y | N |  | 0
463445 | Fax (858) 571-6972 (RWQCB) | 2005-02-01 10:42 | Mike Rosenberg | (858) 614-4132 | City of San Diego | City of San Diego | 2005-01-19 14:42 | 2005-01-19 15:50 | 1 | 68 | 0 | 68 | 1834 Torrence St. | San Diego | 92103 | SD | 6" CP main | 1 | 8/19/2004 | FLOOD DAMAGE | Main break caused overflow | TV crew unit 947 found break in main referred to construction for repair, construction crew made repairs, unit 677 clean roots from MHs75 and63 | N | N | N | None | None | Soaked into canyon | Y | Y | N |  |  | volume estimated per consumers and new mains in area, only one consumer connected to main, no visual accounts prior to this, main not overflowing on arrival.
477409 | Fax (858) 571-6972 (RWQCB) | 2005-01-27 12:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-01-25 17:59 | 2005-01-25 19:35 | 3 | 288 | 150 | 138 | 8971 Jade Coast Ln. | San Diego | 92126 | SD | 8'' VC | 1 | 8-19-2004 | GREASE | Heavy Grease | Contain over flow from entering storm drain system.Returned on 01/27/2005 to flush 2 up and 2 down from fsn#32077.will refer to Area Supervisor,Planners and CCTV to TV Inspect. | N | Y | N | None | None | Soaked into canyon | Y | Y | N |  |  | Called claims for 8971 Jade Coast Ln.(clean up front yard). On 01/27/2005 Crews removed heavy grease from all 5 sections of main .
478169 | Fax (858) 571-6972 (RWQCB) | 2005-01-29 14:48 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2005-01-29 10:16 | 2005-01-29 11:40 | 2 | 168 | 0 | 168 | 1965 SHERIDAN AVE | San Diego | 92103 | SD | 8" PVC | 1 | 08-19-2004 | LINE BREAK | UNKNOWN; REFERRED TO T.V. | MACHINE RODDED TO RELIEVE STOP BUT UNABLE TO ROD WITH LARGE SCREW; REFER TO TV TO DETERMINE POSSIBLE CAUSE; REFER TO AREA SUPEVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | SOAKED IN TO CANYON FLOOR. | Y | Y | N
478199 | Fax (858) 571-6972 (RWQCB) | 2005-01-31 09:00 | Mike Rosenberg | (858) 654-4132 | City of San Diego | City of San Diego | 2005-01-29 18:00 | 2005-01-29 20:00 | 1 | 120 | 0 | 120 | 5620 LA JOLLA BLVD | San Diego | 92037 | SD | 6"VC | 0 | 0 | FLOOD DAMAGE | SEWER MAIN BREAK | SEWER MAIN BREAK ON D/E LINE; CONSUMER ASKED TO STOP USING SERVICES TO STOP 7-31 FROM C/O; STBY NOTIFIED; CONSTRUCTION CREW DISPATCHED. | Y | Y | Y | None | None | PACIFIC OCEAN | Y | Y | N |  |  | Construction Section made repairs to sewer main on 1/29/04. Per County Heath no beach closures or sign posting is necessary.
479105 | Fax (858) 571-6972 (RWQCB) | 2005-02-03 21:05 | Jorge Hernandez | (858) 654-4130 | City of San Diego | City of San Diego | 2005-02-03 15:07 | 2005-02-03 16:00 | 2 | 106 | 60 | 46 | 2705 Meade Av | San Diego | 92104 | SD | 6'' VC | 0 |  | FLOOD DAMAGE | Main break on a dead end main | Contain,Vactored overflow,Flushed main to releive blockage,Will refer to have pipe televise,and do repairs. | N | y | n | None | None | Dissipated in storm box | y | Y | N
479898 | Fax (858) 571-6972 (RWQCB) | 2005-02-11 16:55 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2005-02-08 11:00 | 2005-02-08 14:00 | 20 | 3600 | 2000 | 1600 | DAMON AVE & SANTA FE ST (IN CANYON) | San Diego | 92109 | SD | 24"VC | 0 | 0 | FLOOD DAMAGE | MAIN BREAK | CONSTRUCTION CREW DIVERTED OVERFLOW INTO M/H; MWWD CREWS COMPLETED REPAIRS ON MAIN. | N | Y | Y | None | None | MISSION BAY | Y | Y | Y | Bay/Lagoon/Beach | 3 | County Health notified; advised to post Campland by th Bay; N. Crown Pt; Ski beach boat launch & De Anza boat launch. Spill amount was re-calculated at 20 gpm; Signs were taken down on 2-11-2005.
480991 | Fax (858) 571-6972 (RWQCB) | 2005-02-14 12:00 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2005-02-14 07:46 | 2005-02-14 08:27 | 10 | 410 | 0 | 410 | 4150 UTE DR | San Diego | 92117 | SD | 8"VC | 0 | 0 | GREASE | HEAVY GREASE | MACHINE RODDED TO RELIEVE STOP; CONTACTED CLAIMS FOR 7-33 FROM PRIVATE M/H ON PROPERTY AT SCHOOL; FLUSHED LINES FOR HEAVY GREASE; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | Y | Y | N | None | None | SOAKED INTO SCHOOL GROUNDS & ADJACENT CANYON. | Y | Y | N
482544 | Fax (858) 571-6972 (RWQCB) | 2005-02-22 18:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-02-22 14:30 | 2005-02-22 15:20 | 1 | 50 | 50 | 0 | 5702 Madra Ave | San Diego | 92120 | SD | 8'' VC | 0 |  | ROOTS | root blockage | Relieved root blockage refer to area supervisor and CCTV to inspect 2 up and 2 down from FSN# 57653 | Y | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | FSN# to beTV are 58029,57667,57653,57651&57650.
482741 | Fax (858) 571-6972 (RWQCB) | 2005-03-18 15:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-02-23 13:45 | 1134133.6042 | 5 | 225 | 0 | 225 | 3211 Belle Isle Dr | San Diego | 92105 | SD | 6'' CP | 0 |  | ROOTS | Root Blockage. | relieved stoppage refer to area supervisor and cctv to tv 2 section up and 2 sections down. | Y | Y | N | None | None | Dirt Cayon | Y | Y | N |  | 0 | Refer to FSN's 44929,44928,44546,44930 & 44931to be tv by CCTV
483422 | Fax (858) 571-6972 (RWQCB) | 2005-02-27 22:10 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2005-02-27 19:01 | 2005-02-27 21:05 | 1 | 124 | 0 | 124 | BURLINGAME DR & SAN MARCOS AVE( IN CANYON) | San Diego | 92104 | SD | 8"PVC | 0 | 0 | CONSTRUCTION | APOXY LINING IN M/H CAUSED STOP | HANDRODDED MAIN TO RELIEVE STOP; REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO CANYON FLOOR | Y | Y | N
483500 | Fax (858) 571-6972 (RWQCB) | 2005-03-01 09:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-02-28 08:50 | 2005-02-28 10:10 | 2 | 160 | 160 | 0 | 4381 Oregon Street | San Diego | 92104 | SD | 6" VC | 1 | 02/03/2005 | FLOOD DAMAGE | Main Break | Machine rodded 6'' VC main relieved stoppage and also did 2up and 2 down refer to Area Supervisor and CCTV. | N | N | N | None | None | Concrete Alley. | Y | Y | N |  | 0 | Refer the following FSN 33422,33423,33425&33412 to tv via Swim and 9008.Main break was refer to Construction for repairs ASAP.
486095 | Fax (858) 571-6972 (RWQCB) | 2005-03-16 13:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-03-13 21:00 | 2005-03-13 03:25 | 1 | 385 | 0 | 385 | Timberidge Rd & Corbett Ct | San Diego | 92014 | SD | 8'' PVC | 0 |  | FLOOD DAMAGE | Main Break down stream of m/h35 | Flushed main to relieve stop. | N | Y | N | None | None | Disipated in stormdrain. | Y | Y | N |  |  | Will make report final once cctv completes condition assessment o f724 CCTV confirmed main break
486322 | Fax (858) 571-6972 (RWQCB) | 2005-03-16 13:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-03-14 15:15 | 2005-03-14 16:23 | 2 | 136 | 0 | 136 | 4166 Euclid Av | San Diego | 92105 | SD | 6" unknown | 1 | 11-18-2004 | FLOOD DAMAGE | Main Break on 6'' VC Main | flushed to relieve stop, cleaned up and down stream sections, called for TV crew. | N | Y | N | None | None | Dissipated in storm drain system. | Y | Y | N |  |  | notofied claims via St. 38 for clean-up, CCTV Confirmed main breakon 3/15/05 after Condition assesment request was completed.
487029 | Fax (858) 571-6972 (RWQCB) | 2005-03-30 08:00 | Jose L Oropeza | (858) 615-5772 | City of San Diego | City of San Diego | 2005-03-17 14:30 | 2005-03-17 18:30 | 200 | 48000 | 22000 | 26000 | 123 35th Street | San Diego | 92113 | SD | 10'' VC | 0 |  | LINE BREAK | Manhole and main was Vandalized blocking 10'' VC main | Rodded &Flushed Main To Relieve Stoppage, Setup Portlable Dam in Storm Drain Channel to Contain and Bypass .Sewage Spill Refer to Area Supervisor And CCTV. | N | Y | Y | Chollas Creek | San Diego Bay |  | Y | Y | Y | Crosby Street Park Pier | 9 | Manhole was vandalized with rocks blocking sewer main and causing sewer spill.
488295 | Fax (858) 571-6972 (RWQCB) | 2005-03-28 15:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-03-24 08:50 | 2005-03-24 10:25 | 1 | 95 | 95 | 0 | Entrada Lazanja X Purple Sage | San Diego | 92127 | SD | 8'' VC | 0 |  | LINE BREAK | Manhole was vandalized with Rocks,asphalt and mud | Rodded and Flushed 8'' VC Main to relived blockage cause by vandalism, Refer to Area Supervisor and CCTV Supervisor to TV Main 2 up and 2 Down. | Y | N | N | None | None | Street | Y | Y | N |  | 0 | Manhole was vandalized with Rocks,Mud And Asphalt chunks
488561 | Fax (858) 571-6972 (RWQCB) | 2005-03-25 15:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-03-25 11:20 | 2005-03-25 12:45 | 5 | 425 | 0 | 425 | 52nd Street X Mc Gann Street | San Diego | 92105 | SD | 8'' VC | 1 | 11/29/04 | ROCKS | Rocks Block Main | Rodded main to relieved Blockage Refer to Area Supervisor And CCTV to tv 2up and 2 Down. | Y | Y | N | None | None | Soak in dirt and Vegetation in Canyon | Y | Y | N |  | 0 | Refer the following FSN'S # to CCTV for TV 52537,52556,52539,52558,52557
488673 | Fax (858) 571-6972 (RWQCB) | 2005-03-26 16:45 | D.A. BRANCO | (858) 654-4142 | City of San Diego | City of San Diego | 2005-03-26 08:48 | 2005-03-26 10:10 | 10 | 820 | 0 | 820 | 3705 ROBINSON PL | San Diego | 92103 | SD | 10" VC | 0 | 0 | ROOTS | BLOCKAGE CAUSED BY ROOTS. | MACHINE RODDED TO CLEAR ROOT STOP; CLEANED HEAVY ROOTS FROM M/H593. REFER TO AREA SUPERVISOR FOR FURTHER EVALUATION. | N | N | N | None | None | SOAKED INTO EASEMENT AREA | Y | Y | N
045001 | Clay Clifton | 2/22/05 1530pm | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 2/21/05 1330pm | 2/21/05 1345pm | 5 | 100 | 0 | 100 | 5682 Sweetwater Road | Bonita | 91978 | SD | 590-052-190H | 0 | N/A | Infiltration | Heavy rainfall | Check for infiltration upstream. | Y | N | Y | Sweetwater River | None | N/A | Y | N | N | NO | 0
045002 | Clay Clifton | 4/18/05 1030am | Bill Wiltse | 618-660-2007 | County of San Diego | County of San Diego | 4/17/05 1030am | 4/17/05 1400am | 5 | 700 | 0 | 700 | Whitestone Canyon | Spring Valley | 91978 | SD | 505-22-240G | 0 | N/A | Debris | Contractor knocked off manhole lid, spilling dirt and rocks into system. | Cleaned and CCTV'd up and downstream, locking lid installed. | N | N | N | None | None | Dry, sandy creek bed | Y | N | N | NO | 0
492830 | Fax (858) 571-6972 (RWQCB) | 2005-04-21 19:30 | Jeff Wilder | (858) 654-4130 | City of San Diego | City of San Diego | 2005-04-21 16:31 | 2005-04-21 16:55 | 2 | 48 | 0 | 48 | Russ Bl. X 11th Ave. | San Diego | 92101 | SD | MH 134 Vandalised | 0 | 0 | LINE BREAK | 5 gallon bucket was in MH 134 causing partial blockage | No overflow on arrival, MH cover was wet, MH was up, vacuum down MH and found bucket, pulled bucket out and flow went down to normal. | N | N | N | None | None | Dried up in street | Y | Y | N |  |  | Due to heavy traffic, cleaning two up and two down will be done at a later time. When reporting this to P.D. they said this does not mett their vandalism criteria. Left a messege at storm water pollution per notification plan.
493615 | Fax (858) 571-6972 (RWQCB) | 2005-04-27 15:00 | Jose Luis Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-04-27 12:36 | 2005-04-27 13:15 | 2 | 78 | 50 | 28 | 5th Ave X Washington Street | San Diego | 92103 | SD | 6'' VC | 0 | N/A | ROOTS | Roots Blocking 6'' VC Main. | Rodded 6'' VC Main refer to area supervisor and refer to CCTV to TV 2 up and 2 Down . | N | Y | N | None | None | Decipated into Storm drain System | Y | Y | N |  | 0
493919 | Fax (858) 571-6972 (RWQCB) | 2005-04-29 16:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-04-29 13:33 | 2005-04-29 14:00 | 2 | 54 | 54 | 0 | 3993 Park Blvd | San Diego | 92104 | SD | 6 VC | 0 | N/A | GREASE | Grease Blockage | Flushed and rodded 6'' VC Main Refer to Area Supervisor and CCTV to tv 2up And 2 Down. | N | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | City Crews clean area // There was damages to Church Properety ,Luth & Turley was call out.
493946 | Fax (858) 571-6972 (RWQCB) | 2005-04-29 21:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-04-29 18:40 | 2005-04-29 20:48 | 2 | 256 | 0 | 256 | 3066 Elm Street | San Diego | 92104 | SD | 6'' CP | 0 | N/A | ROOTS | Heavy Roots Blockage | Rodded 6''CP Main refer to area supervisor and CCTV supervisor to tv 2 up and 2 down | N | N | N | None | None | Soak into Canyon | Y | Y | N |  | 0
494006 | Fax (858) 571-6972 (RWQCB) | 2005-04-30 16:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-04-30 12:20 | 2005-04-30 13:15 | 1 | 55 | 0 | 55 | 2431 Willow Street | San Diego | 92106 | SD | 6'' CP | 0 | N/A | ROOTS | Heavy Roots Blockage | Rodded 6''CP Main relieved Blockage refer to area Supervisor and CCTV Supervisor for 2 up And 2 Down. | N | N | N | None | None | Dirt Canyon | Y | Y | N |  | 0
493723 | Fax (858) 571-6972 (RWQCB) | 2005-05-02 09:00 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-04-28 09:25 | 2005-04-28 10:51 | 150 | 12900 | 6500 | 6400 | Hillside Dr X torrey Pines Rd | San Diego | 92037 | SD | 8'' VC | 0 |  | FLOOD DAMAGE | contractor working at p/s 27 running pumps when air valve went inopt contractor error | city forces responded vactor spill ,washdown affected area ,post contaminate signs per county | N | Y | Y | pacific ocean la jolla bay | None |  | Y | Y | Y | scripps pier south to la jolla cove | 4 | As Per Clay Clifton sign were removed by Life Guards on 05/01/2005
494009 | Fax (858) 571-6972 (RWQCB) | 2005-05-04 01:30 | Jeff Wilder | (858) 654-4130 | City of San Diego | City of San Diego | 2005-04-30 11:00 | 2005-04-30 18:30 | 20 | 9000 | 7000 | 2000 | 5050 Santa Fe St | San Diego | 92109 | SD | 24" V.C. | 1 | 02/08/2005 | FLOOD DAMAGE | 24" gravity main Break caused by rain undermining pipe concrete cap. | Contained in concrete channel located at Damon and Mission Bay Dr.. Pumped sewage back into main. | Y | Y | Y | Rose Creek | Mission Bay |  | Y | Y | Y |  | 3 | Per DEH, signs were removed on 5-3-05. 31 signs were removed, 6 signs were missing.
496440 | Fax (858) 571-6972 (RWQCB) | 2005-05-16 15:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-05-16 12:50 | 2005-05-16 13:45 | 5 | 275 | 200 | 75 | 1405 Park Blvd | San Diego | 92134 | SD | 6'' CP | 1 | 04/21/2005 | ROOTS | Root Blockage in 6'' CP main | Rodder rod 6'' cp main relieved root blockage refer to area supervisor and CCTV Supervisor. | N | Y | N | None | None | Dicipated into stormdrain System. | Y | Y | N |  | 0
495478 | Fax (858) 571-6972 (RWQCB) | 2005-06-02 13:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-05-10 12:00 | 2005-05-10 12:35 | 5 | 175 | 175 | 0 | Campanille Dr X Lindo Paseo | San Diego | 92115 | SD | 6'' CP | 0 | N/A | FLOOD DAMAGE | Gravity Main Break | Rodder Relieved blockage refer to Area Supervisor And CCTV Supervisor | N | N | N | None | None | Street Gutter | Y | Y | N |  | 0 | City Crews Recovered Seweage before Entering Storm Drain.
500646 | Fax (858) 571-6972 (RWQCB) | 2005-06-10 12:00 | Mike Dawson | (858) 614-5772 | City of San Diego | City of San Diego | 2005-06-10 07:06 | 2005-06-10 07:45 | 2 | 78 | 0 | 78 | Golfcest Dr X Navajo Rd | San Diego | 92119 | SD | 8'' VC | 0 | N/A | ROOTS | ROOTS AND GREASE | Rodded and flushed main relieved blockage refer to area supervisor and CCTV. | N | Y | N | None | None | Soak into Golf Course Grounds. | Y | Y | N |  | 0 | Stormdrain outlet into Golfcourse.
501745 | Fax (858) 571-6972 (RWQCB) | 2005-06-17 12:00 | MIKE DAWSON | (858) 614-5772 | City of San Diego | City of San Diego | 2005-06-17 06:28 | 2005-06-17 07:28 | 40 | 2400 | 1500 | 900 | 6600 AKINS AVE | San Diego | 92114 | SD | 8'' VC | 1 | 09/15/2004 | GREASE | HEAVY GREASE. | RODDED TO RELIEVE BLOCKAGE FLUSHED TWO UP TWO DOWN WILL REFER TO AREA SUPERVISOR AND CCTV. | N | Y | N | None | None | SOAKED INTO GROUND CHANNEL. | Y | Y | N |  | 0 | CITY CREWS SET UP CONTAINMENT AND RECOVERY OF OVERFLOW.
503195 | Fax (858) 571-6972 (RWQCB) | 2005-06-24 10:30 | Jose L Oropeza | (858) 614-5772 | City of San Diego | City of San Diego | 2005-06-24 08:28 | 2005-06-24 09:15 | 10 | 470 | 300 | 170 | 4405 Vanderver Av | San Diego | 92108 | SD | 8'' VC | 1 | 10/03/04 | GREASE | Heavy Grease | Flushed Main Relieved Grease blockage Refer to area Supervisor & CCTV Supervisor | N | Y | Y | San Diego River | Pacific Ocean |  | Y | Y | N |  | 0 | Per Clay Cliffton No Signs will be posted overflow did not reached any public waters or Pacific Ocean.
045002 | Clay Clifton | 4/18/05 1030am | Bill Wiltse | 619-660-2007 | County of San Diego | County of San Diego | 4/17/05 1030am | 4/17/05 1400am | 8 | 700 | 0 | 700 | Whitestone Canyon | Spring Valley | 91978 | SD | 505-22-240G | 0 | N/A | Debris | Contractor knocked off manhole lid, spilling dirt and rocks into system. | Cleaned and CCTV'd up and downstream - locking lid installed. | N | N | N | None | None | Dry, sandy creek bed | Y | N | N | NO | 0